## CustMeas
MEASURE REFERENCE NUMBER:
| MEASURE DESCRIPTION: |  | << Enter Cells Highlighted in Yellow
CHELAN PUD CUSTOMER NAME:
| ELECTRIC RATE SCH: | 3
| DOMINANT BUILDING TYPE: | 19
| PRIMARY HEAT & COOL SYSTEM: | 1
SERVICE ADDRESS:
CITY, STATE, ZIP CODE:
FACILITY CONTACT:
CONTACT EMAIL:
PHONE NUMBER:
METER NUMBER:
FEDERAL TAX ID NUMBER:
Incentive Check Information (if different than above).
NAME ON INCENTIVE CHECK (Print):
INCENTIVE CHECK MAILING ADDRESS:
INCENTIVE CHECK - CITY, STATE, ZIP CODE:
| TOTAL VFD PURCHASE & INSTALL COSTS: |  | << Enter Total Project Costs Here.
| Maximo #: | 289014
| Account #: | 556000
Electric Meter Service Point #:
PUD Purchase Requisition #:
PUD Purchase Order #:
MEASURE REFERENCE NUMBER:
Demand Savings: | 0 | kW
Total Annual Lighting Energy Saved: | 0 | kWh/Year
AC Benefit:
Electric Heating Penalty: | 0%
Total Annual kWh Savings: | 0 | kWh/Year
Total Annual Busbar Energy Saved: | 0 | kWh/Year
Incentive Unit Amount: | 0.13 | $/kWh/year
Maximum Incentive Amount: | 0
Incentive Amount: | 0
DEFAULT SETTINGS
| SECTOR: | Commercial
| CATEGORY: | Refrigeration-Evaporator Fan VFD's
| SUB-CATEGORY: | Evaporator and Condenser Fans
| BUILDING TYPE: | Industrial Plant with One Shift
| VINTAGE: | Existing
| LOST OPPORTUNITY: | No
| LOCATION: | Heating Zone 1 Cooling Zone 3
| MEASURE LIFE: | 15
| BASIS OF SAVINGS: | Measured and Verified
| ESTIMATED KWH SAVED | 0
ACTUAL/VERIFIED KWH/UNIT SAVED:
| FUNDING SOURCE: | UTILITY FUNDING
| PO DATE TO USE: | PAID
| STATUS (Initial setting, to be updated by CIS): | Preliminary
| MAXIMO WORK ORDER #: | 289014
| GL ACCOUNT #: | 556000
| START DATE: | 2013-02-27 13:55
| PUD Admin Cost / Unit: | 0
Note on D5: Charlie Grist: Select building type from list. If multiple building types are present consider separate audit sheets for separate buildings. Or select the type that most closely matches the primary areas of the building where proposed lighting measures occur. This value is used to estimate interactive effects of lighting energy savings on HVAC.
Note on D6: Charlie Grist: Select dominant space heat type from list. If multiple space heat types are present, consider separate audit sheets for separate buildings. Or select the type that most closely matches the primary areas of the building where proposed lighting measures occur. This value is used to estimate interactive effects of lighting energy savings on HVAC.

## Evap Fan VFDs
Customer Name: | 0
Facility Name: | 0
Contact: | ,
Evaporator Fans
Room/Zone Description | Verified VFD Installed? (Yes,No) | Cond. or Evap. Fan? | VFD Rated HP | Total Cost Estimate | PUD Resource $mart Incentive (65%) | Calc. Annual kWh Saved | Measured Motor kW w/o VFD | Existing Fans Cycled? (Yes,No) | Fan On Date | Fan Off Date | Existing Fan Total Annual kWh | VFD Motor Measure kWh Begin Date | VFD Motor Measure kWh End Date | VFD Motor Total Measured kWh | VFD Motor Total Annual kWh | Measured & Verified Total Annual kWh Saved
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
| No | Evap |  |  |  | 0
|  |  | 0 | 0 | 0 | 0 | 0
Condenser Fans
Room/Zone Description | Verified VFD Installed? (Yes,No) | Cond. or Evap. Fan? | VFD Rated HP | Total Cost Estimate | PUD Resource $mart Incentive (65%) | Calc. Annual kWh Saved | Measured Motor kW w/o VFD | Total Compr. HP Cooled by Tower | Fan On Date | Fan Off Date | Existing Fan Total Annual kWh | VFD Motor Measure kWh Begin Date | VFD Motor Measure kWh End Date | VFD Motor Total Measured kWh | VFD Motor Total Annual kWh | Measured & Verified Total Annual kWh Saved
| No | Cond |  |  |  | 0
| No | Cond |  |  |  | 0
| No | Cond |  |  |  | 0
| No | Cond |  |  |  | 0
| No | Cond |  |  |  | 0
| No | Cond |  |  |  | 0
| No | Cond |  |  |  | 0
|  |  | 0 | 0 | 0 | 0 | 0
|  | TOTAL | 0 | 0 | 0 | 0 | kWh/Year
Incentive Level | 75% | 60% |  |  |  | 0 | Busbar kWh/Year
Costs in this table are based on material purchase and installation estimates provided
by Mike Riley at Schmitt Electric to Jim White on 5/15/09. They include line filters and labor, but do not include sales tax. | [8 empty] | 65% |  | % kWh Savings Discount
These prices are not considered CONFIDENTIAL, but please do not share them out of professional courtesy to the supplier. | [10 empty] | 75%
VFD Rated HP | Price | Unit Comm. Incent. | kWh Savings | Busbar Savings |  | Total Evap. Fan HP | 0 |  | Unit Industrial Incentives | % Cost w/o Sales tax | Ind Incentive $/kWh | Est. No. Installed in 2013 | Est. kWh Saved | Total Commercial Incentives | Customer's Cost | T | Rated HP of VFD | Total Est. Installed Costs | Commercial VFD Incentive | Industrial VFD Incentive
5 | 2755 | 1785.24 | 8903.3333 | 9159.7493 |  | Approx. Capacity Factor | 80% |  | 1934.01 | 64.8% | 0.26735 |  | 0 | 0 | 0 |  | 5 | 2978.155 | 1785.24 | 1934.01 | 0.59944 | 0.6494
7.5 | 2755 | 1785.24 | 13355 | 13739.624 |  | Average Motor Efficiency | 90% |  | 1934.01 | 64.8% | 0.17823 |  | 0 | 0 | 0 |  | 7.5 | 2978.155 | 1785.24 | 1934.01 | 0.59944 | 0.6494
10 | 2827 | 1831.896 | 17806.6667 | 18319.4987 |  | Total Average kW | 0 |  | 1984.554 | 64.8% | 0.13717 |  | 0 | 0 | 0 |  | 10 | 3055.987 | 1831.896 | 1984.554 | 0.59944 | 0.6494
15 | 3186 | 2064.528 | 26710 | 27479.248 |  | Conserv. Load Factor | 50% |  | 2236.572 | 64.8% | 0.10306 |  | 0 | 0 | 0 |  | 15 | 3444.066 | 2064.528 | 2236.572 | 0.59944 | 0.6494
20 | 3505 | 2271.24 | 35613.3333 | 36638.9973 |  | Total Annual kWh | 0 |  | 2460.51 | 64.8% | 0.085033 |  | 0 | 0 | 0 |  | 20 | 3788.905 | 2271.24 | 2460.51 | 0.59944 | 0.6494
25 | 4213 | 2730.024 | 44516.6667 | 45798.7467 |  | Savings, kWh/Year/HP | 1780.6667 | (From Cascade Energy Engr. Study) | 2957.526 | 64.8% | 0.081768 |  | 0 | 0 | 0 |  | 25 | 4554.253 | 2730.024 | 2957.526 | 0.59944 | 0.6494
30 | 4819 | 3122.712 | 53420 | 54958.496 |  | #DIV/0! | 0 | kWh/Year | 3382.938 | 64.8% | 0.077941 |  | 0 | 0 | 0 |  | 30 | 5209.339 | 3122.712 | 3382.938 | 0.59944 | 0.6494
40 | 5574 | 3611.952 | 71226.6667 | 73277.9947 |  | Average MW Saved | 0 | Avg. MW | 3912.948 | 64.8% | 0.067614 |  | 0 | 0 | 0 |  | 40 | 6025.494 | 3611.952 | 3912.948 | 0.59944 | 0.6494
50 | 6639 | 4302.072 | 89033.3333 | 91597.4933 |  | Avg. Cost per kWh = | 0.019 | per kWh | 4660.578 | 64.8% | 0.064426 |  | 0 | 0 | 0 |  | 50 | 7176.759 | 4302.072 | 4660.578 | 0.59944 | 0.6494
60 | 7800 | 5054.4 | 106840 | 109916.992 |  | Annual Cost Savings = | 0 | per Year | 5475.6 | 64.8% | 0.063077 |  | 0 | 0 | 0 |  | 60 | 8431.8 | 5054.4 | 5475.6
[13 empty] | 0 | 0 | 0
Facility | Room Description | [7 empty] | 386.802 |  |  |  | 0 | #DIV/0!
[9 empty] | 257.868 |  |  |  | 4.7 Avg. MW | 0
VFD Rated HP | Cond. or Evap. Fan? | [7 empty] | 198.4554 |  |  |  | 0 | 0.705
5 | Evap | [7 empty] | 149.1048 |  |  |  | 0
VFD Rated HP | Cond. or Evap. Fan? | [7 empty] | 123.0255 |  |  |  | #DIV/0!
7.5 | Evap | [7 empty] | 118.301
VFD Rated HP | Cond. or Evap. Fan? | [7 empty] | 112.7646
10 | Evap | [7 empty] | 97.8237
VFD Rated HP | Cond. or Evap. Fan? | [7 empty] | 93.2116
15 | Evap | [7 empty] | 91.26
VFD Rated HP | Cond. or Evap. Fan?
20 | Evap
VFD Rated HP | Cond. or Evap. Fan?
25 | Evap
VFD Rated HP | Cond. or Evap. Fan?
30 | Evap
VFD Rated HP | Cond. or Evap. Fan?
40 | Evap
VFD Rated HP | Cond. or Evap. Fan?
50 | Evap
VFD Rated HP | Cond. or Evap. Fan?
60 | Evap
VFD Rated HP | Cond. or Evap. Fan?
5 | Cond
VFD Rated HP | Cond. or Evap. Fan?
7.5 | Cond
VFD Rated HP | Cond. or Evap. Fan?
10 | Cond
VFD Rated HP | Cond. or Evap. Fan?
15 | Cond
VFD Rated HP | Cond. or Evap. Fan?
20 | Cond
VFD Rated HP | Cond. or Evap. Fan?
25 | Cond
VFD Rated HP | Cond. or Evap. Fan?
30 | Cond
VFD Rated HP | Cond. or Evap. Fan?
40 | Cond
VFD Rated HP | Cond. or Evap. Fan?
50 | Cond
VFD Rated HP | Cond. or Evap. Fan?
60 | Cond

## Application
COMMERCIAL/INDUSTRIAL REFRIGERATION FAN VFD INCENTIVE APPLICATION
FACILITY NAME: |  |  |  |  | METER NO: | ELECTRIC RATE SCH:
Enter information on Input Sheet |  |  |  |  | Enter information on Input Sheet | Sch. 2, Commercial >40 kW
SERVICE ADDRESS: |  |  |  |  | CITY, STATE, ZIP CODE:
Enter information on Input Sheet |  |  |  |  | Enter information on Input Sheet
FACILITY CONTACT: |  |  |  |  | CONTACT EMAIL:
Enter information on Input Sheet |  |  |  |  | Enter information on Input Sheet
PHONE NUMBER: |  |  | FAX NUMBER: |  | FEDERAL TAX ID NUMBER:
Enter information on Input Sheet |  |  |  |  | Enter information on Input Sheet
NAME ON INCENTIVE CHECK (Print):
Enter information on Input Sheet
INCENTIVE CHECK MAILING ADDRESS: |  |  |  | CITY, STATE, ZIP CODE:
Enter information on Input Sheet |  |  |  | Enter information on Input Sheet
| VFD HP | (A) INCENTIVE LEVEL | (B) UNITS REQUESTED | (A x B) INCENTIVE REQUESTED | ACTUAL UNITS INSTALLED | FINAL INCENTIVE AMOUNT | PUD VERIFIED
| 5 | 1785.24 | 0 | 0
| 7.5 | 1785.24 | 0 | 0
| 10 | 1831.896 | 0 | 0
| 15 | 2064.528 | 0 | 0
| 20 | 2271.24 | 0 | 0
| 25 | 2730.024 | 0 | 0
| 30 | 3122.712 | 0 | 0
| 40 | 3611.952 | 0 | 0
| 50 | 4302.072 | 0 | 0
| 60 | 5054.4 | 0 | 0
| TOTAL |  |  | 0 | (C)
|  |  |  | Actual Labor and Material Cost (Attached receipts and invoices) |  | 0
|  |  | (D) |  | x 75% = (E) | 0
Final Incentive Payment (Lowest of C or E) | [5 empty] | 0
By signing this Application you are acknowledging you have read and agree with the Resource$mart Agreement attached to this form.
CUSTOMER SIGNATURE |  |  |  |  | DATE
Installation of Conservation Measures. Except during Recipient agrees that in order to receive payment from the PUD Recipient must install VFD's with appropriate line filters, and the PUD must receive the invoice for the items described in this agreement within 180 days of the approval of this application. If Recipient is unable to complete the installation and deliver an invoice by this date, this application and approval becomes null and void. Customer must reapply for incentive fund amounts. Incentive funds, if available, may by substantially lower.
Authorization to proceed will be mailed to you within 10 days from date received by the PUD
For Pre-Authorization, mail signed form to: |  |  |  | For Payment: Sign at the appropriate place above and submit a copy of receipts and invoices showing the total cost to purchase and install the variable frequency drives.
Chelan County Public Utility District
Energy Services Dept., Attn: Jim White
PO Box 1231
Wenatchee, WA 98807-1231
To be completed by the PUD
AUTHORIZED BY: |  |  |  |  | DATE
VERIFIED BY: |  |  |  | PO # | MEASURE # | MAXIMO # | ACCOUNT #
[6 empty] | 289014 | 556000

## Cascade Findings (hidden)
Industrial Fruit Warehouse | VFD HP Rating | Peak Fan Load (kW) | Annual kWh Savings | Annual Savings per HP (kWh/HP/Yr) | Load Date | Remove Date | Savings Percent | Avg. Savings/ 10 kW/Month | Comments
Stemilt Growers | 15 | 7.5 | 26710 | 1780.6667 | 1998-09-25 | 1999-04-01 | 72% | 5682.9787 | Savings do not include the fact that fans run all year, even if there is no fruit in the room.
Stemilt Growers | 15 | 7.5 | 25564 | 1704.2667 | 1998-10-05 | 1999-03-27 | 71% | 5910.7514 | Savings do not include the fact that fans run all year, even if there is no fruit in the room.
Trout/Blue Chelan | 15 | 12 | 59193 | 3946.2 | 1998-09-30 | 1999-07-03 | 63.7% | 5361.6848
Blue Bird | 15 | 6.5 | 23862 | 1590.8 | 1998-10-23 | 1999-05-22 | 66.4% | 5219.5406
Blue Star | 20 | 9.5 | 10502 | 525.1 | 1998-09-07 | 1998-11-21 | 57.4% | 4421.8947 | Room only operated for two and half months.
McDougall & Sons | 15 | 12.3 | 16424 | 1094.9333 | 1998-09-14 | 1999-06-07 | 53.7% | 1505.96 | Base case had cycled fans. VFD, not recommended.
Average | 16 | 8.6 | 29166.2 | 1909.4067 | kWh/Year/HP |  | 64.03%
Actual Savings from 2010-2011 Industrial Evap. Fan VFD's | [5 empty] | (Does not include indirect refrigeration savings of 12%)
Columbia Fruit Packers |  |  |  | Stemilt - North Miller |  |  |  | Stemilt - Olds Station
HP | Average Actual kWh/Year Savings | kWh/HP/Year |  | HP | Average Actual kWh/Year Savings | kWh/HP/Year |  | HP | Average Actual kWh/Year Savings | kWh/HP/Year
25 | 36259.6046 | 1450.3842 |  | 25 | 14111.2 | 564.448 |  | 40 | 143664 | 3591.6
HP |  |  |  | HP |  |  |  | HP
20 | 45592.4611 | 2279.6231 |  | 20 | 22574.6554 | 1128.7328 |  | 30 | 75657.2 | 2521.9067
HP |  |  |  | HP |  |  |  | HP
15 | 25852.3229 | 1723.4882 |  | 15 | 44381.4 | 2958.76 |  | 25 | 70824.1847 | 2832.9674
|  |  |  | HP |  |  |  | HP
|  |  |  | 10 | 3204.7415 | 320.4741 |  | 20 | 61805.4345 | 3090.2717
HP
[8 empty] | 15 | 40504.0866 | 2700.2724
To be conservative, the estimated annual savings are
| based on 1,335 kWh/Year/HP. | [6 empty] | HP
[8 empty] | 10 | 13104 | 1310.4

## Condenser Fan Savings (hidden)
Information on this page was created by Dr. Jim White, P.E. on 1/6/10
Used to calculate compressor energy savings when installing 15 HP
variable frequency drive (VFD) on cooling tower fan motor.
The following graph was taken from
SCREW COMPRESSORS: A COMPARISON OF APPLICATIONS AND
FEATURES TO CONVENTIONAL TYPES OF MACHINES
J. Trent Bruce
Toromont Process Systems |  |  |  | 8775
Calgary, Alberta, Canada
The values below were derived by looking at the graph on the right.
% Compressor Capacity | % Power @ 8.0 Compression Ratio | % Power @ 5.0 Compression Ratio | % Power @ 3.0 Compression Ratio
10% | 46% | 40% | 32%
20% | 51% | 43% | 38%
30% | 56% | 50% | 43%
40% | 62% | 55% | 51%
50% | 68% | 62% | 59%
60% | 75% | 70% | 66%
70% | 80% | 79% | 76%
80% | 88% | 84% | 82%
90% | 94% | 93% | 91%
100% | 100% | 100% | 100%
Compressor HP as a function of capacity and pressures
(For 250 HP compressor from Joe Pillis @Frick 1-800-336-7264)
HP vs % Capacity | 25 to 140 psi | 25 to 115 psi | CR = 5.6 | CR = 4.6
100% | 190 | 163 | 100% | 85.79%
20% | 78.3 | 64.8 | 41.21% | 34.11%
12% | 71.7 | 59.1 | 37.74% | 31.11%
kW vs % Capacity | 25 to 140 psi | 25 to 115 psi | kW Difference | kW Saved (50%)
100% | 157.2778 | 134.9278 | 22.35 | 11.175
20% | 64.815 | 53.64 | 11.175 | 5.5875
12% | 59.3517 | 48.9217 | 10.43 | 5.215
|  |  | Est. Avg. kW Saved = | 5.5875
|  |  | 10 Months, Hr/Year = | 7300
|  |  | 15 HP Condenser Fan VFD, kWh Saved/Year = | 40788.75
|  |  | Annual kWh Saved per Cond Fan HP = | 2719.25
Note: Savings do not include direct fan
energy savings on the cooling tower fan motor.
[5 empty] | 455 | 200
[5 empty] | 8760 | 4000
[5 empty] | 3985.8 | 800 | 3185.8
477.87

## Data (hidden)
Index | Select Electric Rate Schedule | Energy Charge, $/kWh | Demand Charge, $/kW | Resource$mart | Sector | Maximo Project
1 | Enter information on Input Sheet | 0 | 0 | 0 |  | 289014
2 | Sch. 2, Commercial <40 kW | 0.027 | 0 | 0.13 | Commercial | 289014
3 | Sch. 2, Commercial >40 kW | 0.0235 | 2.4 | 0.13 | Commercial | 289014
4 | Sch. 3, Industrial | 0.013734 | 3.5207 | 0.15 | Industrial | 260969
5 | Sch. 30, Industrial, Time of Use | 0.013145 | 3.5207 | 0.15 | Industrial | 260969
Index
3 | Sch. 2, Commercial >40 kW | 0.0235 | 2.4 | 0.13 | Commercial | 289014

## Metering (hidden)
Baseline Power Measurements-
Pre-VFD Measurements
15 minute power recording meter set on 4/30/10 on fan 4B
80% | Est. Savings Percentage
| Actual Measured kW | Run Hours/year | kWh/Year | 80% Est. Annual Savings
Fan 1A | 15.7 | 8030 | 126071 | 100856.8
Fan 1B | 16 | 8030 | 128480 | 102784
Fan 2A | 15.9 | 8030 | 127677 | 102141.6
Fan 2B | 15.7 | 8030 | 126071 | 100856.8
Fan 3A | 15.8 | 8030 | 126874 | 101499.2
Fan 3B | 15.7 | 8030 | 126071 | 100856.8
Fan 4A | 15.8 | 8030 | 126874 | 101499.2
Fan 4B | 15.7 | 8030 | 126071 | 100856.8
Total | 126.3 | kW | 1014189 | 811351.2 | kWh/year
17849.7264
48681.072

## LSYield (hidden)
|  |  | Index | Index | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
|  |  | 15 | 8 | [7 empty] | Discounted Levelized $ per therm
| Look-Up Ids |  |  |  |  | Lighting Savings Yield by Predominant Space Heat Fuel Source | [5 empty] | 0.4645 | Load Shape Look Up
Index | 5th Plan Name | ShapeType | Synergy | Spaceheat | Synergy Building Type Name | Electric Resistance | Heat Pump | Gas | Unconditioned | Default Hours of Lighitng | Gas Heat Interaction (therms saved per kWh lighting saved) | Gas Heat NPV per kWh electric lighting saved | Electric Resistance | Heat Pump | Gas | Unconditioned | Default Measure Life
1 | Large Off | LgOff | Enter information on Input Sheet | Enter information on Input Sheet | [13 empty] | Index | Select Electric Rate Schedule | Energy Charge, $/kWh | Demand Charge, $/kW | Resource$mart | SECTOR | Maximo # | GL Account #
2 | Medium Off | LgOff | Office 20,000 to 100,000 sf | Electric Resistance, No AC | Office 20,000 to 100,000 sf | 91.61% | 102% | 107.9% | 100% | 4200 | -0.0081888 | -0.0038037 | ExLgOffElecHt | ExLgOffHtPmpHt | ExLgOffGasHt | ExLgOff | 12 | 1 | Enter information on Input Sheet | 0 | 0 | 0 |  | 289014 | 556000
3 | Small Off | SmOff | Office >100,000 sf | Electric Resistance, w/ AC | Office >100,000 sf | 90.51% | 102% | 106.8% | 100% | 3600 | -0.0081888 | -0.0038037 | ExLgOffElecHt | ExLgOffHtPmpHt | ExLgOffGasHt | ExLgOff | 12 | 2 | Sch. 2, Commercial <40 kW | 0.027 | 0 | 0.06 | Commercial | 289014 | 556000
4 | Big Box | LgRet | Office <20,000 sf | Heat Pump | Office <20,000 sf | 69.09% | 95.5% | 111.7% | 100% | 3000 | -0.021382 | -0.0099319 | ExSmOffElecHt | ExSmOffHtPmpHt | ExSmOffGasHt | ExSmOff | 12 | 3 | Sch. 2, Commercial >40 kW | 0.0235 | 2.4 | 0.06 | Commercial | 289014 | 556000
5 | Small Box | SmRet | Retail Big Box >50,000 sf One-Story | Gas Heat, No Air Cond. | Retail Big Box >50,000 sf One-Story | 81.86% | 102.5% | 111.8% | 100% | 4800 | -0.015013 | -0.0069734 | ExLgRetElecHt | ExLgRetHtPmpHt | ExLgRetGasHt | ExLgRet | 12 | 4 | Sch. 3, Industrial | 0.0135 | 3.23 | 0.15 | Industrial | 260969 | 556000
6 | High End | SmRet | Retail 5,000 to 50,000 sf | Gas w/ Air Cond. | Retail 5,000 to 50,000 sf | 68.09% | 92.5% | 103.4% | 100% | 3900 | -0.017742 | -0.0082413 | ExSmRetElecHt | ExSmRetHtPmpHt | ExSmRetGasHt | ExSmRet | 12 | 5 | Sch. 30, Industrial, Time of Use | 0.0133 | 3.23 | 0.15 | Industrial | 260969 | 556000
7 | Anchor | LgRet | Retail Boutique <5,000 sf | Refrigerated or Cooled | Retail Boutique <5,000 sf | 76.31% | 97.5% | 104.4% | 100% | 3400 | -0.014103 | -0.0065508 | ExSmRetElecHt | ExSmRetHtPmpHt | ExSmRetGasHt | ExSmRet | 12 | Index |  |  |  |  | Commercial
8 | K-12 | School | Retail Anchor Store >50,000 sf Multistory | Unconditioned | Retail Anchor Store >50,000 sf Multistory | 71.08% | 96.5% | 110.1% | 100% | 4000 | -0.019562 | -0.0090866 | ExLgRetElecHt | ExLgRetHtPmpHt | ExLgRetGasHt | ExLgRet | 12 | 2 | Sch. 2, Commercial <40 kW | 0.027 | 0 | 0.06 | Commercial | 289014 | 556000
9 | University | School | School K-12 |  | School K-12 | 56.88% | 86% | 100.4% | 100% | 2400 | -0.021837 | -0.010143 | ExSchoolElecHt | ExSchoolHtPmpHt | ExSchoolGasHt | ExSchool | 12
10 | Warehouse | Wareh | College or University |  | College or University | 68.21% | 95.5% | 110.8% | 100% | 3000 | -0.021382 | -0.0099319 | ExSchoolElecHt | ExSchoolHtPmpHt | ExSchoolGasHt | ExSchool | 12
11 | Supermarket | Groc | Warehouse |  | Warehouse | 61% | 80.5% | 96.36% | 100% | 3500 | -0.017742 | -0.0082413 | ExWarehElecHt | ExWarehHtPmpHt | ExWarehGasHt | ExWareh | 12
12 | MIniMart | Groc | Retail Supermarket | Unconditioned | Retail Supermarket | 85.3% | 97% | 105.2% | 100% | 6500 | -0.010009 | -0.004649 | ExGrocElecHt | ExGrocHtPmpHt | ExGrocGasHt | ExGroc | 12
13 | Restaurant | Rest | Retail Mini Mart |  | Retail Mini Mart | 69.5% | 94.5% | 104.9% | 100% | 6500 | -0.017742 | -0.0082413 | ExGrocElecHt | ExGrocHtPmpHt | ExGrocGasHt | ExGroc | 12
14 | Lodging | Hotel | Restaurant |  | Restaurant | 42.51% | 72.5% | 96.01% | 100% | 5000 | -0.026841 | -0.012468 | ExRestElecHt | ExRestHtPmpHt | ExRestGasHt | ExRest | 12
15 | Hospital | Health | Lodging |  | Lodging | 68.53% | 90% | 104.8% | 100% | 3600 | -0.018197 | -0.0084527 | ExHotelElecHt | ExHotelHtPmpHt | ExHotelGasHt | ExHotel | 12
16 | OtherHealth | Health | Hospital |  | Hospital | 28.91% | 65% | 94.19% | 100% | 5900 | -0.032755 | -0.015215 | ExHealthElecHt | ExHealthHtPmpHt | ExHealthGasHt | ExHealth | 12
17 | Other | CommLight | Other Health, Nursing, Medical Clinic |  | Other Health, Nursing, Medical Clinic | 91.87% | 102% | 108.2% | 100% | 3600 | -0.0081888 | -0.0038037 | ExHealthElecHt | ExHealthHtPmpHt | ExHealthGasHt | ExHealth | 12
18 |  | Ind | Other Commercial |  | Other Commercial | 86.68% | 102% | 103% | 100% | 4000 | -0.0081888 | -0.0038037 | ExCommLight | ExCommLight | ExCommLight | ExCommLight | 12
19 |  | Ind | Industrial Plant with One Shift |  | Industrial Plant with One Shift | 61% | 80.5% | 96.36% | 100% | 2250 | -0.017742 | -0.0082413 | IndShift1 | IndShift1 | IndShift1 | IndShift1 | 12
20 |  | Ind | Industrial Plant with Three Shifts |  | Industrial Plant with Three Shifts | 61% | 80.5% | 96.36% | 100% | 8400 | -0.017742 | -0.0082413 | IndShift3 | IndShift3 | IndShift3 | IndShift3 | 12
21 |  | Flat | Industrial Plant with Two Shifts |  | Industrial Plant with Two Shifts | 61% | 80.5% | 96.36% | 100% | 4500 | -0.017742 | -0.0082413 | IndShift2 | IndShift2 | IndShift2 | IndShift2 | 12
22 |  | StreetLight | Exterior 24 Hour Operation |  | Exterior 24 Hour Operation | 100% | 100% | 100% | 100% | 8760 | 0 | 0 | Flat | Flat | Flat | Flat | 12
23 |  |  | Street & Area Lighting (Photo Sensor Controlled) |  | Street & Area Lighting (Photo Sensor Controlled) | 100% | 100% | 100% | 100% | 5400 | 0 | 0 | StreetLight | StreetLight | StreetLight | StreetLight | 12
24
25 |  |  | Lodging
26
27
28
29
30
Index |  |  | Synergy
15 |  |  | Lodging
Note on G3: Charlie Grist: Lighting Savings Yield is the fraction of lighting energy savings that is realized after taking into account interactions between energy use in the lighting, heating and cooling systems. These values include region-wide estimates of the average saturation of cooling systems. Multiply lighting savings by LSYield to get energy savings net of electric space heat & cooling interactions. Does not include gas interactions. Values are from a series of several hundred DOE 2 runs performed by Mike Kennedy in 2003 on several prototypes in several configurations of shell, lpd, ventilation rates, HVAC system configuration and climate. Adopted by RTF in 2004. Values are default estimates for common cases of building and system configuration and operating conditions thought to represent the population. Over 600 results were synthesized into the categories represented in the tables as a simplification for regional conservation analysis and for default values for the RTF calculators and deemed savings calculations. As a result the default values may not represent specific cases. Specific cases which are thought to have significantly different interactions than the defaults should be modeled under RTF protocols. Original work in file: InteractionsBldgType01082004.xls Default annual hours of lighting operation are estimated from twelve sources by Grist and adopted by RTF in 2004. See file R:\CG\Main\Plan 5\Commercial\Assessment\Data\hours.xls