UNIT OUTAGE EFFECTS ON ROCKY REACH

AND ROCK ISLAND CAPACITIES

Rocky Reach Capacity

Rocky Reach capacity is approximately 1,255 MW at the plant and 1,277 MW with encroachments.

Project capacity will be lower if the headwater reservoir is lower, if the encroachment value is less, or when flows are higher than 200 kcfs.

There is a loss of approximately 15 MW per every foot that the headwater is lower than full.

Decrease in Rocky Reach capacity (MW) for unit outages (includes netted encroachments).

| Unit | All Units Avail. (MW) | Reduction in MW for unit outage |
| --- | --- | --- |
| C1 | 107 | 102 |
| C2 | 107 | 102 |
| C3 | 107 | 102 |
| C4 | 107 | 102 |
| C5 | 107 | 102 |
| C6 | 107 | 102 |
| C7 | 107 | 102 |
| C8 | 132 | 127 |
| C9 | 132 | 127 |
| C10 | 132 | 127 |
| C11 | 132 | 127 |
| Sum | 1,277 |  |

Rock Island Capacity

Rocky Island capacity is approximately 501 MW at the plant and 575 MW with encroachments.

Project capacity will be lower if the headwater reservoir is lower, if the encroachment value is less, or when flows are higher than 220 kcfs.

There is a loss of approximately 14 MW per every foot that the headwater is lower than full.

Decrease in Rock Island capacity (MW) for unit outages (includes netted encroachments).

| Unit | All Units Avail. (MW) | Reduction in MW for unit outage |
| --- | --- | --- |
| B1 | 19.5 | 16.5 |
| B2 | 19.5 | 16.5 |
| B3 | 19.5 | 16.5 |
| B4 | 19.5 | 16.5 |
| B5 | 21.5 | 19.5 |
| B6 | 21.5 | 19.5 |
| B7 | 21.5 | 19.5 |
| B8 | 21.5 | 19.5 |
| B9 | 21.5 | 19.5 |
| B10 | 21.5 | 19.5 |
| U1 | 46.0 | 44 |
| U2 | 46.0 | 44 |
| U3 | 46.0 | 44 |
| U4 | 46.0 | 44 |
| U5 | 46.0 | 44 |
| U6 | 46.0 | 44 |
| U7 | 46.0 | 44 |
| U8 | 46.0 | 44 |
| Sum | 575 |  |