## Hydro Capacity
DRAFT - Updated January 22, 2022 Willard
Capability or Capacity Values For District's Hydro Projects
There are several numbers being used to describe the capacity or capability at the Districts hydro plants. Below is a description of the various ways to calculate the capacity or capability at the plants. Documentation is also provided, so in the future, a person knows where the numbers came from. The suggested numbers for Project Capability are described in Section 1. below, realizing that for various reasons, other numbers (other then 1.) described below may need to be used for various activities. The words capacity and capability generally are used interchangeably.
1. Project Capability
Generator Nameplate Capacity (see section 2.) will be used rounded to even megawatts.
For instance: Rocky Reach has a generator nameplate capacity of 1,300 mw.
If there is a need to use one number, then use the Generator Nameplate Capacity, which is standard in the industry.
Please use these numbers in any official documents.
The 2002 Annual Report has used 1,287 for Rocky Reach and 660 for Rock Island from 1987 to 2002. This showed a total
capability of over 2,000 MW. The 1,287 and 660 will no longer be used, the numbers below in this section will be used.
Because Rocky Reach units C1 through C7 went through a replacement of generators (2003 through 2006),
the numbers for Rocky Reach changed with the Generator Nameplate Capacity increasing for each unit.
Rock Island numbers for Powerhouse 1 may change when units are rehabbed, starting around 2008.
RR & RI numbers will not change when the Attraction Water Turbines are installed, because of round off to whole MWH.
ROUNDED TO EVEN MW, IF YOU WANT MORE DECIMAL PLACES SEE SECTION 2
|  |  | Rocky Reach |  | Nov 2006 |  |  |  |  | Rock Island |  | Oct 2009
|  |  |  | Generator Nameplate Capacity | 1349 | MW |  |  |  |  | Generator Nameplate Capacity | 629.425 | MW
|  |  |  | Lake Chelan | May 2010
|  |  |  | Generator Nameplate Capacity | 59.2 | MW
|  |  |  | Totals (Generator Nameplate Capacity) | 2037 | MW
Changes made:
| 5/10/2011 : | Updated RI Nameplate for B3
| 5/10/2011 : | Updated RI Installed Capacity (Letter to FERC Apr 6, 2011)
| 6/16/2011 : | Changed Nameplate flows in section 2 & added max flows to Section 8 & Added Section 11 Grand Coulee contract
| 9/29/2011 : | Added dates to Best gate changes at RI, Changed EIA-860 numbers for MVAR at RI
| 1/7/2012 : | Section 8: Changed EIA-860 net numbers for Lake Chelan
| 4/18/2012 : | Section 2: Changed the unit flow for RR to maximum flow & Section 7: added individual units
| 12/13/2012 : | Section 2: Updated Rehabbed B9 Turbine HP, Section 3A: B9 Best Gate HP & MW, Section 8: change to 20 Mvar for A-1 & A-2
| 2/8/2013 : | Section 8: Revised B9-B10 EIA-860 numbers & EIA-860 MVAR
| 3/28/2013 : | Section 5: Revised C8-11 Overload Capacity
| 6/11/2013 : | Section 2: Revised B-9 Head & Flow
| 1/8/2014 : | Added a section 7a & 7b
| 2/9/2015 : | Section 2: Updated RI Max Flows
| 5/18/2015 : | Section 2: Updated RI Max Flows
| 2/16/2016 : | Section 7b: Updated RI Capacity due to # of RI1 units unavailable effect on Wanapum Encroachment
| 3/3/2016 : | Section 6-7: Updated RR & RI Capacity
| 5/26/2016 : | Section 7b: Updated RI Capacity
| 10/16/2017 : | Section 2 & 3a: Updated RR & RI Installed Capacity Removed AWT
| 6/6/2018 : | Section 7b: Updated RI Capacity Calculation
| 9/23/2019 : | Section 7b: Updated RI Installed Capacity B6
| 12/12/2022 : | Section 2: Updated C8-C11 Nameplate Capacity & B4 Capacity
2. Generator Nameplate Capacity
This is the rating provided by the manufacturer and stamped on a plate on the generator.
Usually the rating is given as MVA (Mega Volt Amperes) along with a PF (Power Factor).
The MVA times the PF gives the MW (Mega Watt) Generator Nameplate Capacity.
This is different then the Turbine Nameplate Rating that is usually defined in horsepower.
The Maximum Generator Nameplate Capacity is reported to FERC annually on Form EIA-860
The Total Maximum Generator Nameplate Capacity is reported to FERC annually on Form EIA-412.
Rock Island maximum flow from July 2009 study adjusted to a 34.5 gross head which occurs when maximum flow through all units.
Rock Island 2 flow approximately 18.3 kcfs per unit if cavitation limits are off.
Turbine blades welded for B1 @ 75%; B2 @ 77%; B3 & B4 @ 85%; B5 through B7 @ 100% blade tilt.
Also shown are the future Attraction Water Turbines (AWT) with projected operation not known. (Removed Oct 12, 2017)
34.5 ft
|  |  | 84 ft | [7 empty] | Head
|  |  | Head | [6 empty] | Rated | @217 kcfs
|  | Rated | @201 kcfs | [6 empty] | Gross | Max
|  | Net | Max | [6 empty] | Head | Flow | Turbine | Gen. | Gen. | Gen.
| Rocky Reach | Head | Flow | Turbine | Gen. | Gen. | Gen. |  | Rock Island 1 | Feet | KCFS | HP | MVA | PF | MW | Rehab
Rehab |  | Feet | KCFS | HP | MVA | PF | MW |  | B-HU | 32 | 0.5 | 2100 | 1.75 | 0.7 | 1.225
2003-03-31 | C-1 | 92 | 17 | 140000 | 120 | 0.95 | 114 |  | B-1 | 45 | 6.8 | 32000 | 23 | 0.9 | 20.7
2003-11-22 | C-2 | 92 | 17 | 140000 | 120 | 0.95 | 114 |  | B-2 | 45 | 6.8 | 32000 | 23 | 0.9 | 20.7
2006-05-11 | C-3 | 92 | 17 | 140000 | 120 | 0.95 | 114 |  | B-3 | 45 | 6.8 | 32000 | 23 | 0.9 | 20.7
2005-11-08 | C-4 | 92 | 17 | 140000 | 120 | 0.95 | 114 |  | B-4 | 39.7 | 6.8 | 26392 | 23 | 0.9 | 20.7 | 2021-08-20
2006-10-30 | C-5 | 92 | 17 | 140000 | 120 | 0.95 | 114 |  | B-5 | 39.7 | 7.9 | 36530 | 25 | 0.9 | 22.5
2005-05-03 | C-6 | 92 | 17 | 140000 | 120 | 0.95 | 114 |  | B-6 | 39.7 | 7.9 | 36530 | 25 | 0.9 | 22.5 | 2018-04-06
2004-11-17 | C-7 | 92 | 17 | 140000 | 120 | 0.95 | 114 |  | B-7 | 45 | 7.9 | 36530 | 25 | 0.9 | 22.5
2017-12-15 | C-8 | 92 | 20.5 | 190000 | 145 | 0.95 | 137.75 |  | B-8 | 45 | 8.5 | 34000 | 25 | 0.9 | 22.5
2017-04-28 | C-9 | 92 | 20.5 | 190000 | 145 | 0.95 | 137.75 |  | B-9 | 39.7 | 7.9 | 36530 | 25 | 0.9 | 22.5 | 2012-05-01
11-17-2016 | C-10 | 92 | 20.5 | 190000 | 145 | 0.95 | 137.75 |  | B-10 | 39.7 | 8.3 | 33371 | 25 | 0.9 | 22.5 | 2008-05-16
2017-08-17 | C-11 | 92 | 20.5 | 190000 | 145 | 0.95 | 137.75 |  |  |  | 76.1 | 337983 |  |  | 219.025
|  | Total | 201 | 1740000 |  | Total | 1349 | MW |  | Rated
Net
[9 empty] | Rock Island 2 | Head
Rated Flow C1-C7 (16.1 kcfs) & C8-C11 (17.2 kcfs) | [8 empty] | U-1 | 39.7 | 17.5 | 71600 | 54 | 0.95 | 51.3
[9 empty] | U-2 | 39.7 | 17.5 | 71600 | 54 | 0.95 | 51.3
[9 empty] | U-3 | 39.7 | 17.5 | 71600 | 54 | 0.95 | 51.3
[9 empty] | U-4 | 39.7 | 17.5 | 71600 | 54 | 0.95 | 51.3
|  | Rated | [6 empty] | U-5 | 39.7 | 17.5 | 71600 | 54 | 0.95 | 51.3
|  | Net | Max | [5 empty] | U-6 | 39.7 | 17.5 | 71600 | 54 | 0.95 | 51.3
|  | Head | Flow | Turbine | Gen. | Gen. | Gen. |  | U-7 | 39.7 | 17.5 | 71600 | 54 | 0.95 | 51.3
| Lake Chelan | Feet | KCFS | HP | MVA | PF | MW |  | U-8 | 39.7 | 17.5 | 71600 | 54 | 0.95 | 51.3
2009-09-25 | A-1 | 336 | 1.3 | 42662 | 37 | 0.8 | 29.6 |  |  |  | 140 | 572800 |  |  | 410.4
2010-04-30 | A-2 | 336 | 1.3 | 42662 | 37 | 0.8 | 29.6
|  | Total | 2.6 |  |  | Total | 59.2 | MW |  | RI1 & RI2 | 216.1 | 910783 |  | Total | 629.425 | MW
[6 empty] | Project Totals | 2037.625 | MW
[14 empty] | FERC TOTAL | 628.2 | MW
(Minus B-HU )
3A. Current Installed Capacity - Using Best Gate for Determining FERC Annual Charges
FERC in 1995 (FERC order 576) allowed utilities to submit the turbine's most efficient point (Best Gate) for determining size at rated head.
Rocky Reach FERC Exibit A filling 3-31-2007
Lake Chelan change by FERC letter 9-30-2010, 53.6 mw on 1-23-2010 & 59.2 mw on 4-30-2010
Rock Island changes to B3, B5, B6, B7, & B10 letter to FERC Apr 6, 2011 & letter from FERC June 9, 2011
Rock Island changes to B9 with letter to FERC on Dec. 5, 2012
| Rock Island changes to B4 with letter to FERC on Dec. 7, 2022 | [12 empty] | FERC
Amendment
| Rocky Reach | HP | Conv. | MW | [5 empty] | Rock Island 1 | HP | Conv. | MW | Change
| C-1 | 91189 | 0.75 | 68.392 | [5 empty] | B-HU | -- | -- | --
| C-2 | 91189 | 0.75 | 68.392 |  |  |  |  | Generator Limited | B-1 | 27600 | 0.75 | 20.7 | 9/22/2004
| C-3 | 91189 | 0.75 | 68.392 |  |  |  |  | Generator Limited | B-2 | 27600 | 0.75 | 20.7
| C-4 | 91189 | 0.75 | 68.392 |  |  |  |  | Generator Limited | B-3 | 27600 | 0.75 | 20.7 | 6/9/2011
| C-5 | 91189 | 0.75 | 68.392 |  |  |  |  | Generator Limited | B-4 | 26392 | 0.75 | 19.794 | 6/7/2022
| C-6 | 91189 | 0.75 | 68.392 |  |  |  |  | Runners Fixed | B-5 | 30000 | 0.75 | 22.5 | 6/9/2011
| C-7 | 91189 | 0.75 | 68.392 | [5 empty] | B-6 | 19140 | 0.75 | 14.355 | 11/20/2018
| C-8 | 128738 | 0.75 | 96.554 |  |  |  |  | Runners Fixed | B-7 | 30000 | 0.75 | 22.5 | 6/9/2011
| C-9 | 128738 | 0.75 | 96.554 | [5 empty] | B-8 | 24000 | 0.75 | 18 | 9/22/2004
| C-10 | 128738 | 0.75 | 96.554 | [5 empty] | B-9 | 19140 | 0.75 | 14.355 | 1/24/2014
| C-11 | 128738 | 0.75 | 96.554 | [5 empty] | B-10 | 18800 | 0.75 | 14.1 | 6/9/2011
[11 empty] | 250272 |  | 187.704 | MW
| Total Rocky Reach | 1153275 |  | 864.96 | MW
|  | 1153280 | 0.75 | [6 empty] | Rock Island 2
[7 empty] | FERC Plant Maximum Flow |  |  | U-1 | 37300 | 0.75 | 27.975
[6 empty] | RR | 210 | kcfs |  | U-2 | 37300 | 0.75 | 27.975
| Lake Chelan |  |  |  |  | RI | 220 | kcfs |  | U-3 | 37300 | 0.75 | 27.975
1/23/2010 | A-1 | 42662 |  | 29.6 |  | LC | 2.6 | kcfs |  | U-4 | 37300 | 0.75 | 27.975
10/31/2010 | A-2 | 42662 |  | 29.6 | [5 empty] | U-5 | 37300 | 0.75 | 27.975
|  |  | Total | 59.2 | MW |  |  |  |  | U-6 | 37300 | 0.75 | 27.975
[10 empty] | U-7 | 37300 | 0.75 | 27.975
[10 empty] | U-8 | 37300 | 0.75 | 27.975
|  |  | Project Totals | 1335.664 | MW | [5 empty] | 298400 |  | 223.8 | MW
[10 empty] | Total Rock Island | 548672 |  | 411.504 | MW
[11 empty] | 548672 | 0.75
3B. Old Installed Capacity (pre-2004) - Used for Determining FERC Annual Charges
FERC approved BEST GATE Calculation in 2004, Therefore these numbers were used before the change.
Most of the time it is the same number as Generator Nameplate Rating (except for Rocky Reach)
The new generators being installed at Rocky Reach (2003-2007) will not affect this number (they are turbine limited).
Note, the House unit at Rock Island is not in the total.
Rocky Reach Attraction Water Turbine is a 774 kW unit, with the FERC application rounded to 800 kW.
| Rocky Reach | HP/MVA | Conv/PF | MW | [5 empty] | Rock Island 1 | MVA | PF | MW
| C-1 | 140000 | 0.75 | 105 | Turbine Limited |  |  |  |  | B-HU | -- | -- | --
| C-2 | 140000 | 0.75 | 105 | Turbine Limited |  |  |  |  | B-1 | 23 | 0.9 | 20.7
| C-3 | 140000 | 0.75 | 105 | Turbine Limited |  |  |  |  | B-2 | 23 | 0.9 | 20.7
| C-4 | 140000 | 0.75 | 105 | Turbine Limited |  |  |  |  | B-3 | 16.667 | 0.9 | 15.0003
| C-5 | 140000 | 0.75 | 105 | Turbine Limited |  |  |  |  | B-4 | 23 | 0.9 | 20.7
| C-6 | 140000 | 0.75 | 105 | Turbine Limited |  |  |  |  | B-5 | 25 | 0.9 | 22.5
| C-7 | 140000 | 0.75 | 105 | Turbine Limited |  |  |  |  | B-6 | 25 | 0.9 | 22.5
| C-8 | 132 | 0.95 | 125.4 | [5 empty] | B-7 | 25 | 0.9 | 22.5
| C-9 | 132 | 0.95 | 125.4 | [5 empty] | B-8 | 25 | 0.9 | 22.5
| C-10 | 132 | 0.95 | 125.4 | [5 empty] | B-9 | 25 | 0.9 | 22.5
| C-11 | 132 | 0.95 | 125.4 | [5 empty] | B-10 | 25 | 0.9 | 22.5
| AWT | 1105 |  | 0.8 | [5 empty] | AWT |  |  | 0.7
|  |  | Total | 1237.4 | MW | [7 empty] | 212.8003 | MW
Rock Island 2
| Lake Chelan | [8 empty] | U-1 | 54 | 0.95 | 51.3
| A-1 | 30 | 0.8 | 24 | [5 empty] | U-2 | 54 | 0.95 | 51.3
| A-2 | 30 | 0.8 | 24 | [5 empty] | U-3 | 54 | 0.95 | 51.3
|  |  | Total | 48 | MW |  |  |  |  | U-4 | 54 | 0.95 | 51.3
[10 empty] | U-5 | 54 | 0.95 | 51.3
[10 empty] | U-6 | 54 | 0.95 | 51.3
|  |  | Project Totals | 1908.6003 | MW |  |  |  |  | U-7 | 54 | 0.95 | 51.3
[10 empty] | U-8 | 54 | 0.95 | 51.3
[13 empty] | 410.4 | MW
[12 empty] | Total Rock Island | 623.2003 | MW
4. Dependable Capacity - FERC Required Number for License Applications
This is a non-defined term that FERC requires in license applications. It is up to the licensee to calculate.
In general it is usually calculated for how long and high can the plant generate, when the utility has it's highest peak load.
| Rocky Reach | 1225 | MW | For 4 hours, Based on lowest flow of 82 KCFS in highest demand months Jan-Feb & 4 foot pond
| Rock Island | 542 | MW | From RI License application, with an encroached tailwater. (Wanapum encr. averages 70 MWH)
| Lake Chelan | 66 | MW | Based on average elevation of 1090 in Jan. for 62 plus 4 MW of RR Encroachment.
In 2006 there has been an effort to standardize the calculation of dependable capacity in the Northwest.
Therefore these numbers may change.
5. Continuous Overload Capability
This is what each unit can continuously generate at its maximum at either nameplate or overloaded condition.
Generation at these levels goes beyond the manufacturer's guaranteed nameplate ratings for some units.
Conditions have to be perfect and there would need to be a very high gross head.
Attraction Water Turbines are not included because of the size (RR-0.8 & RI-0.7).
Rocky Reach
After Feb. 2007 |  | MVA | PF | MW |  |  |  |  | Rock Island 1 | MVA | PF | MW
| C-1 | 120 | 0.95 | 114 |  |  |  |  | B-HU | 1.75 | 0.7 | 1.225
| C-2 | 120 | 0.95 | 114 |  |  |  |  | B-1 | 23 | 0.9 | 20.7
| C-3 | 120 | 0.95 | 114 |  |  |  |  | B-2 | 23 | 0.9 | 20.7
| C-4 | 120 | 0.95 | 114 |  |  |  |  | B-3 | 23 | 0.9 | 20.7
| C-5 | 120 | 0.95 | 114 |  |  |  |  | B-4 | 23 | 0.9 | 20.7
| C-6 | 120 | 0.95 | 114 |  |  |  |  | B-5 | 25 | 0.9 | 22.5
| C-7 | 120 | 0.95 | 114 |  |  |  |  | B-6 | 25 | 0.9 | 22.5
| C-8 | 145 |  | 132 |  |  |  |  | B-7 | 25 | 0.9 | 22.5
| C-9 | 145 |  | 132 |  |  |  |  | B-8 | 25 | 0.9 | 22.5
| C-10 | 145 |  | 132 |  |  |  |  | B-9 | 25 | 0.9 | 22.5
| C-11 | 145 |  | 132 |  |  |  |  | B-10 | 25 | 0.9 | 22.5
|  |  | Total | 1326 | MW | [6 empty] | 219.025 | MW
Rock Island 2
[9 empty] | U-1 |  |  | 54
[9 empty] | U-2 |  |  | 54
[9 empty] | U-3 |  |  | 54
[9 empty] | U-4 |  |  | 54
[9 empty] | U-5 |  |  | 54
|  | Maximum | [6 empty] | U-6 |  |  | 54
|  | Turbine |  |  |  | One Unit |  |  | U-7 |  |  | 54
| Lake Chelan | HP |  |  |  | Running |  |  | U-8 |  |  | 54
| A-1 | 44525 |  | 32 |  | 35 | [5 empty] | 432 | MW
| A-2 | 44525 |  | 32 |  | 35
|  |  | Total | 64 | MW | [5 empty] | Total Rock Island | 651.025 | MW
[11 empty] | Project Totals | 2041.025 | MW
6. Hourly Coordination Maximum Capacity with Encroachments
This is the maximum switchyard generation that has been attained by the project, including any encroachments.
With full ponds at project and downstream project
This capacity will decrease at RR & RI for flows above 201 kcfs & 217 kcfs
| Rocky Reach | 1251 | 5/21/2007 @ 16:20 | [5 empty] | Rock Island | 167 | RI1 Generation (Rehabed B9 added 2)
|  | 3 | Addition for HW to 707 | [5 empty] | 7/8/09 Capacity Study | 336 | RI2 Generation
|  | 26 | RI Encroachment | [6 empty] | 60 | RI-1 Wanapum Encr.
|  | -3 | Lake Chelan Encr. | [6 empty] | 35 | RI-2 Wanapum Encr.
|  | 1277 | MW | [6 empty] | -26 | RR Encroachment
| Maximum Flow | 201 | KCFS 84 ft Gross Head | [6 empty] | 572 | Revised 10-14-09 due to rehabbed units B3 & B10
Note: | PNUCC re-regulated shows RR capability at 1,242 | [7 empty] | Maximum Flow | 217 | KCFS 7-6-99 @ 01:00 34.5 Gross Head
RI2 140 kcfs, RI1 76.7 kcfs
| Lake Chelan | 62 | [8 empty] | Wanapum @ 570
|  | 3 | RR Encroachment | [8 empty] | TW 578.5
|  | 65 | MW | [5 empty] | Project Totals | 1914 | MW
| Maximum Flow | 2.6 | KCFS
*See Section 8 for individual units (WECC Net Capacity MW)
7. Hourly Coordination Maximum Capacity without Encroachments
Maximum generation at the switchyards disregarding encroachments
With full ponds at project and downstream project
This capacity will decrease at RR & RI for flows above 201 kcfs & 217 kcfs
| Rocky Reach | 1251 | 5/21/2007 @ 16:20 | [5 empty] | Rock Island | 167 | RI1
|  | 3 | Addition for HW to 707 | [6 empty] | 336 | RI2
|  | 1254 | MW | [5 empty] | Revised 10-14-09, rehabbed units B3, B9, & B10 | 503 | MW
[5 empty] | C1-C7 (105 MW) & C8-C11 (130 MW) = 1,255 MW |  | B1-B4 (15) + B5-B8 (17) + B9-B10 (19) + U1-U8 (42) = 502 MW
| Lake Chelan | 62 | MW | [5 empty] | Project Totals | 1819 | MW
*See Section 8 for individual units (Net EIA-860 MW))
7a. Rocky Reach Hourly Coordination Maximum Capacity without Encroachments
At 201 kcfs assume RI-RR Encroachment around 26 mw
| Total |  |  |  |  | At 201 kcfs assume Lake Chelan Encroachment around 3 mw
| River | RR | Capability
| Flow | Capability | W/ Encroach. |  | C1-C7 | C8-C11
| kcfs | mw | mw |  | mw | mw | Total
| 20 | 1254 | 1277 |  | 104.9 | 129.9 | 1254
| 40 | 1254 | 1277 |  |  |  | 1277 | with Encroachments
| 60 | 1254 | 1277
| 80 | 1254 | 1277 |  | For Units Unavailable and project flows are below 201 kcfs:
| 100 | 1254 | 1277 |  | For C1-C7 reduce total by 95 MW
| 120 | 1254 | 1277 |  | Fore C8-C11 reduce total by 118 MW
| 140 | 1254 | 1277
| 160 | 1254 | 1277 |  | Apply a 15 mw per ft GH factor to Maximum Capability
| 180 | 1254 | 1277 |  | Optimum GH = 707 - 0.00004877*(Flow)^2 + 0.04685121*Flow + 611.61136573
| 200 | 1254 | 1277 |  | Feet Difference = Current GH - Optimum GH
| 220 | 1217 | 1241.4609 |  | MAX CAP = MAX CAP + 15 * Feet Difference
| 240 | 1199 | 1222.7589
| 260 | 1180 | 1204.0568 |  | Apply a RI_RR Encroachment factor to Max Cap
| 280 | 1161 | 1185.3548 |  | RI_RR_Enc Offset = 26 - Current RI_RR_Enc
| 300 | 1143 | 1166.6528 |  | MAX CAP = MAX CAP + RI_RR_Enc Offset
[10 empty] | Highest Instantaneous Generation at Switchyard | 1251 |  | 5-21-2007 @ 16:20
[10 empty] | Highest Instantaneous Generation at Switchyard if HW was at 707 | 1254 |  | 84 ft Head & 201 kcfs
[10 empty] | Highest Instantaneous Generation at the Units | 1262 |  | 5-21-2007 @ 16:20
[10 empty] | Highest Instantaneous Generation at the Units if HW was 707 | 1265
7b. Rock Island Hourly Coordination Maximum Capacity without Encroachments
At 217 kcfs assume Wanapum Encroachment around 95 mw
| Total | [7 empty] | At 217 kcfs assume RR Encroachment around 26 mw
| River | RI | Capability |  | B1-B4 | B5,B7,B8 | B6,B9,B10 | U1-U8
| Flow | Capability | W/ Encroach. |  |  | Capability
| kcfs | mw | mw |  | mw | mw | mw | mw | Totals
| 20 | 505 | 574 |  | 15 | 17 | 19 | 42.1 | 504.8 | @ 34.5' head & Wanapum @ 571.5
| 40 | 505 | 574 | [5 empty] | 574 | with Encroachments
| 60 | 505 | 574
| 80 | 505 | 574 |  | For Units Unavailable:
| 100 | 505 | 574 |  | Reduce MAX CAP for B1-B4 by 12 MW
| 120 | 505 | 574 |  | Reduce MAX CAP for B5-B10 by 15 MW
| 140 | 505 | 574 |  | Reduce MAX CAP for U1-U8 by 39 MW
| 160 | 505 | 574
| 180 | 505 | 574 |  | Apply a 10 mw per ft GH factor to Maximum Capability; While 6 RI1 units unavailable
| 200 | 505 | 574 |  | Delta GH = (RI HW - 613) + (573.5 - TWS) | [5 empty] | (Revised May 2018)
| 220 | 505 | 574 |  | MAX CAP = MAX CAP + (Delta GH * 10 MW)
| 240 | 495 | 564
| 260 | 494.5352 | 563.5352
| 280 | 476.4225 | 545.4225 |  | Apply a Wanapum Encroachment (WanEnc) factor to Max Cap
| 300 | 458.3098 | 527.3098 |  | Change in WanEnc Delta = 5.2 * (571.5 - Wan HW)
MaxWanEnc = 95 - 3 * # of RI1 Units Unavailable
WanEnc Offset = MaxWanEnc - Current WanEnc - WanEnc Delta
If RI Total Flow > 90 kcfs then WanEncOffset = 0
MAX CAP = MAX CAP + WanEnc Offset
[10 empty] | Highest Hourly Generation at Switchyard | 495 |  | 4-21-2000 @ EOH 01:00
[10 empty] | With RI And Wanapum Full Ponds | 495 | Previous number used between 9-10-07 & Nov 2009
[10 empty] | July 8, 2009 Plant Capacity Study | 501 |  | 7/8/2009 with Wanapum at 570'
[10 empty] | Rehabbed B9 | 503
8. Maximum Capacity for WECC and EIA-860 Reports
For the WECC report the Unit Capacity that can be used at the project which includes Encroachment.
For the EIA-860 report the Unit Capacity that can be used at the project which excludes Encroachment.
The numbers are the same for Winter Net Capacity or Summer Net Capacity.
|  |  |  | Net | [8 empty] | Net |  |  | 34.5 ft
|  |  | WECC | EIA-860 |  |  | @ Low Head |  |  |  |  | WECC | EIA-860 |  |  | @ Low Head
|  | EIA-860 | Net | @ 201 |  |  | Maximum |  |  |  | EIA-860 | Net | @ 217 |  |  | Maximum
|  | Nameplate | Capacity | kcfs | MVAR |  | Flow |  |  |  | Nameplate | Capacity | Unit | MVAR |  | Flow
| Rocky Reach | MW | MW | MW | Absorption | Output | KCFS |  |  | Rock Island 1 | MW | MW | MW | Absorption | Output | KCFS
| C-1 | 114 | 107.1 | 104.9 | -20 | +35 | 17 |  |  | B-HU | 1.225 | 1 | 1 | 0 | 0 | 0.5
| C-2 | 114 | 107.1 | 104.9 | -20 | +35 | 17 |  |  | B-1 | 20.7 | 19 | 15 | -3 | +10 | 6.8
| C-3 | 114 | 107.1 | 104.9 | -20 | +35 | 17 |  |  | B-2 | 20.7 | 19 | 15 | -3 | +10 | 6.8
| C-4 | 114 | 107.1 | 104.9 | -20 | +35 | 17 |  |  | B-3 | 20.7 | 19 | 15 | -3 | +10 | 6.8
| C-5 | 114 | 107.1 | 104.9 | -20 | +35 | 17 |  |  | B-4 | 20.7 | 19 | 15 | -3 | +10 | 6.8
| C-6 | 114 | 107.1 | 104.9 | -20 | +35 | 17 |  |  | B-5 | 22.5 | 21 | 17 | -3 | +10 | 7.9
| C-7 | 114 | 107.1 | 104.9 | -20 | +35 | 17 |  |  | B-6 | 22.5 | 21 | 17 | -3 | +10 | 7.9
| C-8 | 137.75 | 132.1 | 129.9 | -20 | +35 | 20.5 |  |  | B-7 | 22.5 | 21 | 17 | -3 | +10 | 7.9
| C-9 | 137.75 | 132.1 | 129.9 | -20 | +35 | 20.5 |  |  | B-8 | 22.5 | 21 | 17 | -3 | +10 | 8.5
| C-10 | 137.75 | 132.1 | 129.9 | -20 | +35 | 20.5 |  |  | B-9 | 22.5 | 22 | 19 | -5 | +10 | 7.9
| C-11 | 137.75 | 132.1 | 129.9 | -20 | +35 | 20.5 |  |  | B-10 | 22.5 | 22 | 19 | -5 | +10 | 8.3
| Total Rocky Reach | 1349 | 1278.1 | 1253.9 |  |  | 201 |  |  |  | 219.025 | 205 | 167 |  |  | 76.1
|  |  |  | @385 ft | [5 empty] | Rock Island 2
|  |  | WECC | Net EIA-860 | [5 empty] | U-1 | 51.3 | 45.9 | 42 | -5.4 | +20 | 17.5
|  | EIA-860 | Net | @ 2.56 |  |  | Maximum |  |  | U-2 | 51.3 | 45.9 | 42 | -5.4 | +20 | 17.5
|  | Nameplate | Capacity | kcfs | MVAR |  | Flow |  |  | U-3 | 51.3 | 45.9 | 42 | -5.4 | +20 | 17.5
| Lake Chelan | MW | MW | MW | Absorption | Output | KCFS |  |  | U-4 | 51.3 | 45.9 | 42 | -5.4 | +20 | 17.5
| A-1 | 29.6 | 31 | 31.4 | -10 | +20 | 1.3 |  |  | U-5 | 51.3 | 45.9 | 42 | -5.4 | +20 | 17.5
| A-2 | 29.6 | 31 | 30.7 | -10 | +20 | 1.3 |  |  | U-6 | 51.3 | 45.9 | 42 | -5.4 | +20 | 17.5
| Encroachment |  | 3 |  |  |  | 2.6 |  |  | U-7 | 51.3 | 45.9 | 42 | -5.4 | +20 | 17.5
| Total Lake Chelan | 59.2 | 65 | 62.1 | MW |  |  |  |  | U-8 | 51.3 | 45.9 | 42 | -5.4 | +20 | 17.5
[11 empty] | 410.4 | 367.2 | 336 |  |  | 140
| Project Totals | 2037.625 | 1915.3 | 1819 | MW
[10 empty] | Total Rock Island | 629.425 | 572.2 | 503 | MW |  | 216.1
9. Project Capability or Capacity with regard to Canadian Entitlement Allocation
Canadian Entitlement Allocation (CEA-EA)
During the High Load Hours (HLH), there is a CEA-EA obligation of Rocky Reach 68 MW and Rock Island 33 MW.
The Participants of RR & RI have an obligation to deliver their percentage share to BPA, who then delivers to BC Hydro.
10. Pre-Encroached Plant Capability
This is the capability that could be realized if there was no encroachment from the downstream plant.
For Rock Island this can be calculated based on A) the tables in the Wanapum encroachment agreement,
or, B) using the maximum generation numbers and adding to them (they will be different but close).
The reason the Rock Island number is larger then previous numbers described, is that 1/2 of the Wanapum
encroachment on Rock Island Powerhouse 2 is normally lost.
For Lake Chelan it can be based on highest observable generation plus Rocky Reach encroachment.
For Rocky Reach the number would be the same as the maximum generation with encroachments,
without the Lake Chelan Encroachment.
| Rocky Reach | 1251 | 5/21/2007 @ 16:20 | [6 empty] | 159 | RI1 Generation
|  | 3 | Addition for HW to 707 | [5 empty] | 4/21/2000 EOH 01:00 | 336 | RI2 Generation
|  | 26 | RI Encroachment | [6 empty] | 60 | RI-1 Wanapum Encr.
|  | 1280 | MW | [6 empty] | 35 | RI-2 Wanapum Encr.
[10 empty] | 40 | Other 1/2 of RI-2 Wan. Encr.
| Lake Chelan | 62 | [7 empty] | 630 | MW @ 215 kcfs
|  | 3 | RR Encroachment
|  | 65 | MW
[9 empty] | Project Totals | 1975 | MW
11. Installed Capacities for Columbia Basin Debris Control (Grand Coulee)
These are the numbers used for allocating Garand Coulee costs for removing debris in the river.
These should be the same numbers as section 3A with the AWT removed
|  |  | Minus | [6 empty] | Minus
|  | 3A. | AWT | [5 empty] | 3A. | AWT
| Rocky Reach | 864.96 | 0 | = | 864.96 |  |  | Rock Island | 411.504 | 0 | = | 411.504
Note on A79: Commissioning dates C1: Exciters 10/26/1995, Transformers 10/18/1996, Turbine Runners 3/31/2003, Governors 3/31/2003, Stator Soleplates 3/31/2003, Generator 3/31/2003
Note on A80: Commissioning dates C2: Exciters 10/29/1996, Transformers 10/18/1996, Turbine Runners 4/11/1999, Governors 4/11/1999, Stator Soleplates 4/11/1999, Generator 11/22/2003
Note on A81: Commissioning dates C3: Exciters 3/6/1998, Transformers 3/9/1998, Turbine Runners 3/12/1998, Governors 3/12/1998, Stator Soleplates 3/12/1998, Generator 5/11/2006
Note on A82: Commissioning dates C4: Exciters 6/3/1997, Transformers 5/27/1997, Turbine Runners 5/30/1997, Governors 5/30/1997, Stator Soleplates 5/30/1997, Generator11/8/2005
Note on A83: Commissioning dates C5: Exciters 12/18/1996, Transformers 12/16/1996, Turbine Runners 12/20/1996, Governors 12/20/1996, Stator Soleplates 12/20/1996, Generator 10/30/06
Note on A84: Commissioning dates C6: Exciters 2/22/1996, Transformers 2/10/1996, Turbine Runners 2/23/1996, Governors 10/7/1997, Stator Soleplates 10/7/1997, Generator 5/3/2005
Note on A85: Commissioning dates C7: Exciters 7/15/1997, Transformers 7/7/1996, Turbine Runners 7/15/1996, Governors 7/15/1996, Stator Soleplates 7/15/1996, Generator 11/17/2004
Note on A86: Commissioning dates C8: Exciters 8/30/1995, Transformers 3/23/1997, Turbine Runners 12/31/1999, Governors 12/31/1999, Stator Soleplates 12/31/1999, Generator 12/31/1999 Transformer Upgrade 6/2/2002 Generator Rewind 12/15/2017
Note on A87: Commissioning dates C9: Exciters 7/26/1995, Transformers 12/4/1998, Turbine Runners 12/4/1998, Governors 12/4/1998, Stator Soleplates 12/4/1998, Generator 12/4/1998 Transformer Upgrade 7/14/2002 Generator Rewind 4/28/2017
Note on A88: Commissioning dates C10: Exciters 6/14/1995, Transformers 2/11/2001, Turbine Runners 8/5/2001, Governors 8/5/2001, Stator Soleplates 8/5/2001, Generator 8/5/2001, Transformer Upgrade 4/28/2001 Generator Rewind 11/17/2016
Note on A89: Commissioning dates C11: Exciters 5/15/1995, Transformers 4/29/2001, Turbine Runners 8/18/2002, Governors 8/18/2002, Stator Soleplates 8/18/2002, Generator 8/18/2002, Transformer Upgrade 4/28/2002 Generator Rewind 8/17/2017
Note on D103: Raised from 2.5 to 2.6 kcfs per WA-DOE 401 Certification # 9389 dated July 16, 2012
Note on P108: FERC Letter 12-5-2012
Note on N149: FERC Order dated 06/09/2011 414,100 kW, effective on June 1, 2003; 418,600 kW, effective on April 1, 2008; 414,700 kW, effective on May 16, 2008; 420,400 kW, effective September 1, 2009; 424,900 kW, effective on June 1, 2010; and 422,212 kW, effective March 1, 2012, which are the on-line operating dates of the upgraded units B6, B5, B10, B3, B7, and B9, respectively. Letter to FERC dated Dec. 5, 2012 reducing B9 to 14.355 and total reduced to 421.255 MW FERC approved 1-24-2014 FERC Order Oct 12, 2017 removed AWT for total of 420.555 FERC Order Nov 20, 2018 changed rehabed B6 for total of 412.410 FERC Filling Jun 7, 2022 changed rehabbed B4 for total 411.504
Note on D259: Raised from 2.5 in July 2012 DOE 401 Water Quality Certification
Note on E363: From revised MWH report 9/7/2011 and modified for max flow of 2.5 kcfs. Will go to from 31.1 to 31.4 & from 30.5 to 30.7 after FERC allows flows to 2.6 kcfs