## Disclaimer
Disclaimer of completeness and accuracy of data provided to evaluate slice product
The information contained in this spreadsheet or report was queried from a database. Chelan PUD disclaims any warranty or representation that this information is completely accurate. Individual entries in the database may contain inaccuracies that could be reflected in this information. If you have any questions, please call Janet Jaspers: janet.jaspers@chelanpud.org or Mike Bradshaw: mike.bradshaw@chelanpud.org

## Rocky Reach
Rocky Reach Forced (unplanned) outages
> 5 hour duration
Jan 1, 2006 through Dec 31, 2020
ID | Hydro | Unit | Reason | Date Off | Date On | Duration Hours | Derating
38 | RR | C-2 | EXCITER TROUBLE | 2006-01-09 05:25 | 2006-01-09 15:10 | 10
97 | RR | C-5 | UNIT FAILING TO START | 2006-11-08 08:14 | 2006-11-08 15:07 | 7
111 | RR | C-4 | SOFTWARE TIMEOUT ON STARTUP | 2006-12-30 06:11 | 2006-12-30 17:01 | 11
113 | RR | C-4 | 86M, BATTERY GROUNDS, START TIMOUT | 2007-01-04 05:22 | 2007-01-04 11:58 | 7
127 | RR | C-8 | GOVERNOR CPU FAILURE | 2007-03-04 05:30 | 2007-03-04 12:24 | 7
181 | RR | C-2 | GEN GUIDE BRG HI VIBRATION Y-AXIS | 2007-09-13 16:52 | 2007-09-14 18:04 | 25
185 | RR | C-3 | GENERATOR GUIDE BEARING TEMP HIHI/86M LOCKOUT RELAY TRIP | 2007-10-04 01:10 | 2007-10-04 08:16 | 7
201 | RR | C-10 | C-10 UNIT NOT IN PRESTART CONDITION AFTER SHUTDOWN | 2007-12-13 23:35 | 2007-12-14 06:42 | 7
258 | RR | C-11 | OIL SEAL LEAK IN C-11 ACB ENCLOSURE | 2008-08-23 15:25 | 2008-08-30 08:57 | 162
267 | RR | C-4 | EXCITER TROUBLE 86G GENERATOR LOCKOUT TRIP | 2008-09-23 18:58 | 2008-09-24 16:01 | 21
281 | RR | C-3 | 86-M WICKET GATE DEVIATING FROM SETPOINT | 2008-11-04 17:55 | 2008-11-05 03:32 | 10
351 | RR | C-2 | BAD SVE ON GATE SERVO, CAN'T GET IT TO SMOOTH OUT | 2009-02-10 09:11 | 2009-02-10 14:54 | 6
370 | RR | C-2 | BLADE CONTROL ISSUES | 2009-03-09 07:52 | 2009-03-09 13:19 | 5
395 | RR | C-2 | RUNNER BLADE VIBRATION | 2009-05-20 05:55 | 2009-05-20 14:46 | 9
423 | RR | C-5 | GENERATOR PHASE A-B, B-C AND C-A VOLTAGE LOW IN ALARM(ALL PHASE VOLTAGES READING 6.2KV AT TIME THE UNIT WAS STOPPED) | 2009-07-30 01:29 | 2009-07-30 09:49 | 8
426 | RR | C-10 | 86T TRIP LOCKOUT | 2009-08-11 02:05 | 2009-08-11 08:48 | 7
427 | RR | C-11 | 86T TRIP LOCKOUT | 2009-08-11 02:06 | 2009-08-11 08:48 | 7
428 | RR | C-6 | GEN PHASE VOLTAGES LOW | 2009-08-13 01:52 | 2009-08-13 08:12 | 6
557 | RR | C-9 | C-9 TURBINE PIT SUMP FLOATS NORMAL AND EMERGENCY FLOATS FAILED TO OPERATE, HIGH WATER LEVEL LEAKING WATER INTO TURBINE GUIDE BEARING OIL | 2010-07-04 01:19 | 2010-07-04 08:59 | 8
572 | RR | C-11 | 86G LOCKOUT RELAY TRIP/DGP RELAY B PHASE DIFFERENTIAL | 2010-08-25 09:04 | 2010-08-27 18:32 | 57
739 | RR | C-6 | ROTOR INSPECTION REASON: MO | 2012-04-20 04:02 | 2012-04-20 19:51 | 16
770 | RR | C-6 | 86M L.O. OPERATED | 2012-07-29 12:11 | 2012-07-29 20:28 | 8
776 | RR | C-5 | 86T RELAY OPERATION/U-1 | 2012-08-13 16:12 | 2012-08-14 14:54 | 23
816 | RR | C-8 | 86G TRIP | 2012-11-16 17:09 | 2012-11-16 23:31 | 6
G014328 | RR | C8 | ARC Net Comm Failure | 2013-02-04 04:56 | 2013-02-05 23:59 | 43
G014338 | RR | C7 | Turbine Guide bearing bad level sensing device | 2013-02-06 13:02 | 2013-02-07 23:59 | 35
G014408 | RR | C10 | Tripped offline | 2013-03-25 21:29 | 2013-03-26 23:59 | 26
G014410 | RR | C10 | Investigation of blade-gate timing relationship | 2013-03-26 08:50 | 2014-04-17 04:50 | 9284
G014473 | RR | C3 | Quide bearing oil level transducer problem. | 2013-04-29 14:40 | 2013-04-29 23:59 | 9
G014638 | RR | C1 | Clean Trash Racks. High differentials | 2013-07-12 03:10 | 2013-07-12 08:50 | 6
G014639 | RR | C2 | Clean Trash Racks. High Differentials | 2013-07-12 03:10 | 2013-07-12 08:50 | 6
G014640 | RR | C3 | Clean Trash Racks. High Differentials | 2013-07-12 03:10 | 2013-07-12 08:50 | 6
G014698 | RR | C1 | High trash rack differential. | 2013-08-07 13:15 | 2013-08-08 03:10 | 14
G014699 | RR | C1, C2, C3 | Clamming and diving on trash racks This derate (940 MW) does NOT include C-10. | 2013-08-08 03:10 | 2013-08-08 09:50 | 7
G014701 | RR | C1 | High Trashrack Differential | 2013-08-08 13:35 | 2013-08-11 23:59 | 82
G014732 | RR | C2 | Unit tripped on a blade deviation | 2013-08-18 02:27 | 2013-08-19 23:59 | 46
G014817 | RR | C8 | Investigating turbine servo rod condition | 2013-09-23 19:00 | 2014-02-14 06:50 | 3444
G014818 | RR | C9 | Investigating turbine servo rod condition | 2013-09-23 19:00 | 2014-01-20 06:50 | 2844
G014819 | RR | C11 | Investigating turbine servo rod condition | 2013-09-23 19:00 | 2013-12-27 08:00 | 2269
G014913 | RR | C4 | Tripped out | 2013-10-17 01:19 | 2013-10-18 23:59 | 47
G014931 | RR | C2 | Unit will not Sync | 2013-10-26 07:14 | 2013-10-26 23:59 | 17
G014961 | RR | C4 | Tripped during startup | 2013-11-07 03:18 | 2013-11-07 23:59 | 21
G014976 | RR | C4 | C-4 to unavailable on start-up. Software timeout | 2013-11-16 03:58 | 2013-11-18 23:59 | 68
G014985 | RR | C2 | Forced out due to headgate issues. | 2013-11-24 17:50 | 2013-11-25 23:59 | 30
G014992 | RR | C7 | Exciter trouble. | 2013-12-01 16:50 | 2013-12-02 23:59 | 31
G015116 | RR | C7 | Exciter problem | 2013-12-21 04:23 | 2013-12-21 23:59 | 20
G015146 | RR | C6 | 86 Relay | 2014-01-24 14:43 | 2014-01-24 23:59 | 9
G015160 | RR | C11 | Locked out on start-up | 2014-02-03 06:13 | 2014-02-04 23:59 | 42
G015193 | RR | C4 | Tripped to lockout on startup | 2014-02-17 06:10 | 2014-02-18 23:59 | 42
G015199 | RR | C1 | Unit PLC failure | 2014-02-22 06:32 | 2014-02-22 23:59 | 17
G015224 | RR | C9 | River conditions due to Wanapum forebay drafting | 2014-03-02 01:16 | 2014-03-03 23:59 | 47
G015225 | RR | C11 | Due to high head across dam, while drawing down level at Rock Island | 2014-03-02 01:16 | 2014-03-03 23:59 | 47
G015226 | RR | C8 | C-8 declared unavailable due to Wanapum forebay drafting | 2014-03-02 01:16 | 2014-03-03 23:59 | 47
G015227 | RR | C8 | Unavailable due to increased head across the dam, while lowering Rock Island Headwater to assist repairs at Wanapum Dam | 2014-03-02 23:54 | 2014-03-03 23:59 | 24
G015228 | RR | C9 | Unavailable due to increased head across the dam, while lowering Rock Island Headwater to assist repairs at Wanapum Dam | 2014-03-02 23:55 | 2014-03-03 23:59 | 24
G015229 | RR | C11 | Unavailable due to increased head across the dam, while lowering Rock Island Headwater to assist repairs at Wanapum Dam | 2014-03-02 23:55 | 2014-03-03 23:59 | 24
G015238 | RR | C8 | Gross head up to 95.5 feet. | 2014-03-03 22:57 | 2014-03-04 23:59 | 25
G015239 | RR | C9 | Gross head up to 95.5 feet. | 2014-03-03 22:57 | 2014-03-04 23:59 | 25
G015240 | RR | C11 | Gross head up to 95.5 feet. | 2014-03-03 22:57 | 2014-03-04 23:59 | 25
G015244 | RR | C7 | Exciter tripped, unable to reset | 2014-03-07 11:05 | 2014-03-07 23:59 | 13
G015357 | RR | C11 | Unit would not start | 2014-04-20 19:42 | 2014-04-21 23:59 | 28
G015362 | RR | C11 | Burnt smell coming from unit - investigating. | 2014-04-22 04:04 | 2014-06-27 19:00 | 1599
G015427 | RR | C1 | Fish screen needs to be removed from intake. | 2014-05-13 07:00 | 2014-05-13 23:59 | 17
G015433 | RR | C7 | Leak at C-7 Main Transformer. | 2014-05-15 07:00 | 2014-05-16 23:59 | 41
G015483 | RR | C1 | Blade devation lockout | 2014-05-29 19:42 | 2014-05-31 19:00 | 47
G015501 | RR | C4 | Unit out due to PLC failure | 2014-06-05 20:50 | 2014-06-06 23:59 | 27
G015522 | RR | C1 | Tripped to lockout on exciter internal trip | 2014-06-16 19:45 | 2014-06-17 23:59 | 28
G015528 | RR | RR Plant | RC requests RR max cap to 850 MW due to N-1 if Sickler bank opens. Changed to 950MW at 0757, then to 1000MW at 0828. To 950MWs at 0939. | 2014-06-18 05:50 | 2014-06-19 18:00 | 36 | various, see reason column
G015670 | RR | RR Plant | Forced reduction due to loss of transmission resources. | 2014-08-05 16:47 | 2014-08-05 22:45 | 6 | 650
G015671 | RR | RR Plant | Forced reduction due to loss of transmission resources. | 2014-08-05 22:45 | 2014-08-06 03:42 | 5 | 900
G015678 | RR | C06 | Tripped on turbine guide bearing low oil. | 2014-08-09 16:31 | 2014-08-09 22:32 | 6
G015686 | RR | C10 | Failed to start | 2014-08-12 20:41 | 2014-08-13 10:28 | 14
G015819 | RR | C04 | C-4 Turbine Guide Bearing (TGB) oil pot is leaking. Repairs could be performed within the first day, unsure of what we'll find when we drop the pot so we gave ourselves an extra day just in case. | 2014-10-09 07:10 | 2014-10-10 18:29 | 35
G015831 | RR | C03 | Failed to start | 2014-10-15 21:00 | 2014-10-16 15:23 | 18
G015868 | RR | C09 | Turbine Guide Bearing (TGB) leaking oil. | 2014-11-12 06:10 | 2014-11-18 15:34 | 153
G015993 | RR | C03 | Exciter trouble | 2014-11-21 06:50 | 2014-11-22 23:59 | 41
15-00257 | RR | C08 | Large unit repairs concerning the stator, rotor and servo rod assembly. This outage replaced G016088 per Peak RC's request | 01/21/2015 16:38 | 12/13/2017 09:19 | 25360.6833
G016427 | RR | RR Plant | Technicians need to go through units C1 - C7 to remove pre-start on packing flow and to complete governor upgrades. They will only need one unit out at a time and they estimate the duration to be less than one hour per unit. I will subimit another TOA for February 19th however it might be shortened or cancelled depending on how well theTech's do on the 18th. This TOA is reflecting a 105 MW derate from RR's 1255 MW total. | 2015-02-18 08:10 | 2015-02-18 13:37 | 5 | 1150
G016500 | RR | C02 | Dive on surface collector | 2015-03-26 10:10 | 2015-03-26 15:50 | 6
G016568 | RR | C04 | 86 lockout on startup | 2015-04-27 13:41 | 2015-04-28 13:43 | 24
G016569 | RR | C04 | Investigate failures during recent startups. Governor problems: Gate Distributor is not working correctly and needs to be cleaned. | 2015-04-30 07:10 | 2015-05-01 18:37 | 35
G016711 | RR | C10 | Hot smell from windings | 2015-06-24 19:17 |  | 0
G016711 | RR | C10 | COIL FAILURE and STATOR REWIND | 2015-06-24 19:17 | 2016-11-17 07:28 | 12276
G016716 | RR | RR Plant | C-2 trashrack into alarm. Divers needing C-1, C-2 and C-3 outages to safely perform the cleaning. | 2015-07-01 03:09 | 2015-07-01 11:50 | 9 | 950
G016723 | RR | C09 | Breaker pump excessive run time. No prestarts. | 2015-07-06 01:55 | 2015-07-06 06:28 | 5
G016868 | RR | C06 | High Field Voltage. Extending outage for continuation of Rotor damage assessment. Extending outage for repairs and testing. | 2015-08-06 15:24 | 2015-08-28 16:18 | 529
G016996 | RR | C03 | Phase 3 software timeout. | 2015-09-07 02:28 | 2015-09-08 23:59 | 46
G017084 | RR | C06 | Investigate / repair Turbo Vent Valve vibration. | 2015-09-22 08:10 | 2015-09-22 15:18 | 7
G017210 | RR | C06 | Unit breaker problems. | 2015-10-21 15:03 | 2015-10-22 13:08 | 22
G017270 | RR | C03 | To change out C-3 transformer sudden pressure device. | 2015-11-06 07:10 | 2015-11-06 16:20 | 9
G017361 | RR | C02 | Forced Outage resulting from G017236 - Blade Trunnion Gap measurement and Rotor bus bar inspection and Shaft Oil Seal inspection | 2015-12-04 16:51 | 2015-12-11 16:05 | 167
G017401 | RR | C04 | Possible exciter problems, operator investigating. | 2015-12-24 06:14 | 2015-12-24 14:29 | 8
G017402 | RR | C04 | Exciter problems | 2015-12-24 15:06 | 2015-12-26 09:29 | 42
G017603 | RR | C01 | High Trashrack Differential | 2016-03-02 06:30 | 2016-03-07 07:10 | 121 | 85
G017685 | RR | C07 | C-7 tripped the 86 lockout due to turbine guide bearing Hi Hi vibration on start up. | 2016-04-01 06:09 | 2016-04-01 12:48 | 7
G017996 | RR | C09 | COIL FAILURE and STATOR REWIND | 07/14/2016 23:18 | 04/28/2017 13:59 | 6902.6833
G018163 | RR | RR Plant | C06, C04 & C03 THRUST POT INSPECTIONS | 2016-09-13 07:12 | 2016-09-13 14:40 | 7 | 1149
G018164 | RR | RR Plant | C02 & C01 THRUST POT INSPECTIONS | 2016-09-15 07:11 | 2016-09-15 18:50 | 12 | 1149
G018176 | RR | C02 | Field voltage still unstable at startup. | 2016-09-15 20:01 | 2016-09-16 10:47 | 15
G018279 | RR | C05 | 2016 THRUST POT REPAIRS | 2016-10-12 10:01 | 2016-12-02 14:02 | 1228
G018385 | RR | C10 | Unit tripped on high temp | 2016-11-15 18:35 | 2016-11-16 23:59 | 29
G018408 | RR | RR Plant | TRASH RACK CLEANING on C11, C10 and C9 | 2016-11-27 22:12 | 2016-11-28 05:50 | 8 | 1124
G018409 | RR | RR Plant | TRASH RACK CLEANING ON C8, C7, C6 and C5 | 11/28/2016 22:16 | 11/29/2016 05:22 | 7.1
G018410 | RR | RR Plant | TRASH RACK CLEANING ON C6, C5, C4 and C3 | 11/29/2016 22:09 | 11/30/2016 05:44 | 7.5833
G018413 | RR | C10 | C-10 INSPECTION for TGB OIL LEAK | 2016-11-22 08:11 | 2016-11-22 16:50 | 9
G018414 | RR | C10 | C10 TGB SEAL INSPECT & REPLACE As of Wed Nov 23rd I believe the plan is to have this outage take the place of the C-11 outage. | 11/28/2016 05:50 | 12/01/2016 17:36 | 83.7667
G018417 | RR | C11 | Smoke alarm and burnt smell 12/9/16 Return date extended until the end of January. KR 1/5/2017 return date extended until Nov 2018. AS | 11/27/2016 06:29 | 01/26/2017 06:10 | 1439.6833
G018688 | RR | C01 | Turbine shaft is leaking and needs tightened | 03/08/2017 19:35 | 03/09/2017 14:28 | 18.8833
G018738 | RR | C01 | Hi trash rack differential | 03/21/2017 03:11 | 03/22/2017 23:59 | 44.8
17-07028 | RR | C07 | Determine why it failed to start | 2017-04-02 17:45 | 2017-04-03 16:08 | 22.3833
17-07327 | RR | C01 | Head gates will be installed on Monday (5-8-17) and wiremen will then perform rotor and bus cleaning to resolve exciter alarms. Paul Resler has recommended that we not run C1 throughout the weekend so it will remain unavailable until wiremen can perform the necessary cleaning. | 05/05/2017 15:50 | 05/09/2017 19:08 | 99.3
17-07499 | RR | C05 | RR C-5 tripped offline due to Blade Deviation. Would not restart | 06/23/2017 01:24 | 06/23/2017 10:50 | 9.4333
17-07503 | RR | C05 | troubleshooting | 2017-06-23 22:49 | 06/24/2017 09:31 | 10.7
17-07553 | RR | C04 | Failed to start would not build up voltage | 07/14/2017 07:58 | 2017-07-14 13:47 | 5.8167
17-07632 | RR | C02 | Troubleshoot Thrust Bearing Pad Low Pressure | 2017-08-11 01:06 | 2017-08-11 14:51 | 13.75
17-07668 | RR | C04 | Rotor Weld Crack Warranty Extension of iTOA 17-07633 | 2017-08-21 07:15 | 2017-08-25 15:45 | 104.5
17-07830 | RR | C09 | Try to determine what is causing noise on startup | 10/18/2017 09:51 | 11/27/2017 06:10 | 956.3167
17-07888 | RR | C01 | Exciter voltage alarms and rotor cleaning | 11/06/2017 10:59 | 2017-11-09 14:56 | 75.95
17-07930 | RR | C07 | Tech's testing issue of blade/gate deviation and frequency issues. | 12/01/2017 09:07 | 2017-12-01 16:12 | 7.0833
17-07948 | RR | C08 | Large unit repairs concerning the stator, rotor and servo rod assembly. This outage replaced G016088 per Peak RC's request and is a continuation of 15-00257 | 12/13/2017 16:00 | 12/15/2017 14:00 | 46
1-00541113 | RR | C01 | investigate oil leak | 10/01/2018 17:50 | 01/16/2018 09:45 | 6200.0833
1-00602790 | RR | C01 | oil leak | 10/05/2018 23:59 | 10/02/2018 05:07 | 90.8667
| RR | C01 | unit out of service - inspection for seal leaks | 10/02/2018 05:07 | 10/01/2018 17:50 | 11.2833
1-00601762 | RR | C02 | Troubleshoot exciter issues on shutdown | 09/29/2018 23:59 | 09/28/2018 05:06 | 42.8833
1-00543055 | RR | C02 | shaft seal packing adjustment | 01/19/2018 15:50 | 01/19/2018 14:10 | 1.6667
1-00548793 | RR | C02 | Repair ground | 02/18/2018 23:59 | 02/15/2018 07:02 | 88.95
1-00617008 | RR | C02 | C2 unavailable due to water in the turbine guide bearing oil. | 12/13/2018 23:59 | 12/12/2018 02:07 | 45.8667
1-00620704 | RR | C03 | Troubleshoot the brushes rubbing on the slip rings. | 12/31/2018 17:50 | 12/24/2018 12:15 | 173.5833
1-00602829 | RR | C03 | Change out the oil in the turbine guide bearing on C-3 | 10/03/2018 23:59 | 10/02/2018 13:36 | 34.3833
1-00545853 | RR | C04 | Turbine guide bearing problems | 02/01/2018 17:50 | 02/01/2018 14:08 | 3.7
1-00591184 | RR | C05 | C05 failed to start. Reason unknown. | 08/17/2018 23:59 | 08/16/2018 11:42 | 36.2833
1-00595058 | RR | C05 | Troubleshoot Mech lockout on shutdown | 08/31/2018 23:59 | 08/30/2018 03:51 | 44.1333
1-00591156 | RR | C05 | Plant mechanics to clean SVE on C5. | 08/16/2018 11:50 | 08/16/2018 09:10 | 2.6667
1-00598640 | RR | C07 | Troubleshoot unit trip | 09/19/2018 23:59 | 09/18/2018 08:09 | 39.8333
1-00596238 | RR | C07 | Troubleshoot and restore. | 09/06/2018 23:59 | 09/05/2018 17:11 | 30.8
| RR | C07 | Change oil on turbine guide bearing | 09/11/2018 23:59 | 09/10/2018 08:15 | 39.7333
1-00544196 | RR | C08 | Extension of previous outage. Unit is making a knocking sound. Dewatering unit to investigate. | 02/09/2018 23:59 | 01/28/2018 17:50 | 294.15
1-00571354 | RR | C08 | Wiremen, Techs and Engineers are troubleshooting C8. New Sync Transducer was installed but the unit is not able to start back up. Problem is unknown at this time. | 05/24/2018 13:50 | 05/23/2018 09:50 | 28
1-00572294 | RR | C08 | Unit will need to be dewatered to complete repairs on packing. | 06/18/2018 16:50 | 05/25/2018 13:50 | 579
| RR | C08 | Exciter repair | 09/13/2018 23:59 | 09/12/2018 06:50 | 41.15
1-00569807 | RR | C10 | Investigate vibration shutdown | 05/16/2018 23:59 | 05/14/2018 14:11 | 57.8
| RR | C10 | Tripped offline. Reason unknown. | 06/09/2018 09:50 | 06/09/2018 09:33 | 0.28333
1-00559039 | RR | C10 | Head cover packing | 03/30/2018 23:59 | 03/29/2018 11:05 | 36.9
| RR | C10 | unknown | 05/14/2018 23:59 | 05/13/2018 23:58 | 24.0167
1-00620372 | RR | C10 | Broken Shear Pin | 12/26/2018 23:59 | 12/25/2018 09:40 | 38.3167
1-00570507 | RR | C11 | Troubleshoot unit trip and the smell of smoke | 05/18/2018 23:59 | 05/17/2018 19:19 | 28.6667
1-00593201 | RR | C11 | Gas up breaker. | 08/22/2018 11:50 | 08/22/2018 08:30 | 3.3333
1-00593875 | RR | C11 | Repair SF6 leak | 08/25/2018 17:00 | 08/24/2018 08:06 | 32.9
1-00599581 | RR | RR Plant | Trash Rack Clam stuck in front of C-3 | 09/22/2018 23:59 | 09/21/2018 13:45 | 34.2333
| RR | C01 | 7099 - Other turbine problems | 2019-01-01 | 2019-12-31 23:59 | 8759.9833
| RR | C09 | 4830 - Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 2019-01-01 | 2019-12-31 23:59 | 8759.9833
| RR | C03 | 9300 - Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 2019-07-22 19:26 | 2019-07-27 08:02 | 108.6
| RR | C04 | 3620 - Main transformer | 2019-07-22 19:26 | 2019-07-26 16:20 | 92.9
| RR | C06 | 4551 - Generator bearings | 2019-08-28 16:54 | 2019-09-19 10:15 | 521.35
| RR | C08 | 7050 - Turbine governor | 2019-09-06 21:21 | 2019-09-11 18:47 | 117.4333
| RR | C10 | 3618 - Other switchyard equipment ? (not outside management control) | 2019-09-11 07:10 | 2019-09-11 18:05 | 10.9167
| RR | C11 | 3618 - Other switchyard equipment ? (not outside management control) | 2019-09-11 07:10 | 2019-09-11 18:05 | 10.9167
| RR | C08 | 7007 - Bearings A | 2019-09-18 07:50 | 2019-10-01 15:33 | 319.7167
| RR | C07 | 4551 - Generator bearings | 2019-09-27 16:18 | 2019-12-31 23:59 | 2287.6833
| RR | C02 | 7099 - Other turbine problems | 2019-10-11 15:47 | 2019-12-31 23:59 | 1952.2
| RR | C11 | 7099 - Other turbine problems | 2019-10-11 16:19 | 2019-10-18 08:43 | 160.4
| RR | C06 | 4550 - Generator bearings and lube oil system (including thrust bearings on hydro units) | 2019-12-18 19:43 | 2019-12-20 15:28 | 43.75
| RR | C01 | 7099 - Other turbine problems | 2020-01-01 | 2020-03-13 16:25 | 1744.4167
| RR | C02 | 7099 - Other turbine problems | 2020-01-01 | 2020-01-24 06:50 | 558.8333
| RR | C03 | 7099 - Other turbine problems | 2020-01-01 | 2020-02-27 07:34 | 1375.5667
| RR | C07 | 4560 - Generator vibration (excluding vibration due to failed bearing and other components) | 2020-01-01 | 2020-03-05 | 1536
| RR | C02 | 9015 - Pandemic | 2020-03-23 15:30 | 2020-04-30 06:00 | 902.5
| RR | C07 | 9015 - Pandemic | 2020-03-23 15:30 | 2020-04-30 06:00 | 902.5
| RR | C04 | 4550 - Generator bearings and lube oil system (including thrust bearings on hydro units) | 2020-03-28 07:18 | 2020-03-30 12:58 | 53.6667
| RR | C11 | 7099 - Other turbine problems | 2020-03-28 15:02 | 2020-03-28 23:47 | 8.75
| RR | C05 | 7099 - Other turbine problems | 2020-04-10 17:46 | 2020-04-11 10:11 | 16.4167
| RR | C11 | 7099 - Other turbine problems | 2020-04-24 09:03 | 2020-04-24 15:13 | 6.1667
| RR | C11 | 7099 - Other turbine problems | 2020-04-28 10:04 | 2020-04-28 16:39 | 6.5833
| RR | C09 | 7050 - Turbine governor | 2020-06-30 15:48 | 2020-07-01 14:27 | 22.65
| RR | C11 | 7099 - Other turbine problems | 2020-07-22 17:50 | 2020-08-06 11:02 | 353.2
| RR | C09 | 3982 - PLC - hardware problems (including card failure) | 2020-09-22 23:13 | 2020-09-23 10:01 | 10.8
| RR | C10 | 4551 - Generator bearings | 2020-09-25 09:01 | 2020-09-25 14:32 | 5.5167
| RR | C05 | 4810 - Generator output breaker | 2020-11-09 21:26 | 2020-11-12 15:28 | 66.0333

## Rock Island
Rock Island Forced (unplanned) outages
> 5 hour duration
Jan 1, 2006 through Dec 31, 2020
ID | Hydro | Unit | Reason | Date Off | Date On | Duration Hours | Derating
46 | RI | B-7 | 86-G RELAY TRIP | 2006-01-23 05:07 | 2006-01-23 10:46 | 6
48 | RI | B-7 | 86 G RELAY TRIP | 2006-01-24 00:20 | 2006-01-25 16:16 | 40
52 | RI | U-2 | HAD TO REPLACE REC1 RELAY FOR GATE LOCKS | 2006-02-14 05:18 | 2006-02-14 11:30 | 6
58 | RI | B-6 | IGC FAILURE | 2006-04-24 04:45 | 2006-04-24 17:30 | 13
59 | RI | B-5 | 86G RELAY TROUBLE LOCKOUT OPERATION | 2006-05-02 11:06 | 2006-05-04 14:15 | 51
60 | RI | B-4 | B-4 VACUUM VENT VALVE STUCK OPEN AND FLOODED THE PIT GOT IT TO SHUT BUT UNTIL CHECKED OUT WILL DECLARE UNAVAILABLE AS PER RIENHART | 2006-05-15 21:45 | 2006-05-16 18:33 | 21
76 | RI | B-2 | IGC LO DUE TO OVER VOLTAGE SPIKE | 2006-09-05 16:40 | 2006-09-07 12:35 | 44
90 | RI | U-2 | GENERATOR BACKUP GROUND TRIP | 2006-10-30 09:38 | 2006-10-30 15:00 | 5
101 | RI | U-1 | CT WIRES ROLLED, CAUSING CO2 BANK TO DUMP ON U-1 | 2006-11-22 14:25 | 2006-11-24 13:30 | 47
122 | RI | U-5 | PRESTARTS NOT SATISFIED | 2007-02-13 06:21 | 2007-02-13 15:02 | 9
157 | RI | B-6 | HI VIBRATION ON START UP | 2007-07-19 09:35 | 2007-07-20 12:33 | 27
167 | RI | U-4 | BROKEN PIPE IN GOV TANK, REPORTED BY R. ALEXANDER | 2007-08-03 16:45 | 2007-08-04 15:37 | 23
172 | RI | B-6 | BROKEN SHEAR PIN | 2007-08-27 10:32 | 2007-08-30 23:10 | 85
183 | RI | B-1 | IGC FAILURE, WON'T RESET. BURNT ELECTRONICS SMELL | 2007-10-01 23:40 | 2007-10-02 09:10 | 10
192 | RI | B-6 | BRAKES APPLIED (ON THEIR OWN) ON START-UP | 2007-10-12 12:34 | 2007-10-12 17:51 | 5
216 | RI | U-5 | CARBON SEAL HI TEMP. | 2008-03-18 11:40 | 2008-03-18 18:47 | 7
222 | RI | B-7 | BRAKE SHOES NEED TO BE REPLACED | 2008-03-28 14:24 | 2008-03-31 18:31 | 76
240 | RI | U-5 | GATE LOCKS AND BRAKES NOT SHOWING RELEASED ON START-UP | 2008-06-15 11:30 | 2008-06-15 22:26 | 11
241 | RI | B-9 | SLIP RINGS DAMAGED | 2008-06-16 14:54 | 2008-06-16 20:40 | 6
247 | RI | B-10 | UNABLE TO CONTROL VARS | 2008-07-19 03:30 | 2008-07-19 16:15 | 13
249 | RI | B-10 | EXCITER HIGH TEMP TRIP | 2008-07-22 23:50 | 2008-07-24 17:39 | 42
252 | RI | U-7 | LO ACC. LEVEL. BLADES | 2008-07-27 11:37 | 2008-07-29 15:07 | 52
264 | RI | U-2 | BROKEN SHEAR PIN | 2008-09-14 21:03 | 2008-09-15 09:08 | 12
271 | RI | B-1 | NO WICKET GATE MOVEMENT | 2008-10-07 00:01 | 2008-10-07 19:35 | 20
270 | RI | B-2 | NO GENERATOR VOLTAGE | 2008-10-07 00:24 | 2008-10-13 17:15 | 161
277 | RI | U-3 | SMOKING CELERON SEALS | 2008-10-20 14:07 | 2008-12-08 14:58 | 1177
280 | RI | U-7 | BROKEN SHEAR PIN | 2008-10-25 03:32 | 2008-10-25 09:30 | 6
297 | RI | B-10 | 86 RELAY WILL NOT RE-SET | 2008-11-24 02:50 | 2008-11-24 10:33 | 8
304 | RI | B-6 | AIR GAP LOW ALARM | 2008-12-05 05:13 | 2008-12-09 14:05 | 105
323 | RI | B-HU | IGC SHOWING HIGH INTERMEDIATE GUIDE BRG AND U.S. THRUST BRG TEMPS. ANALOG PAGE ON CPU SHOW NORMAL TEMPS | 2009-01-05 03:24 | 2009-01-06 09:44 | 30
345 | RI | B-5 | 86 LO ON SHUT DOWN | 2009-01-28 04:31 | 2009-01-28 14:52 | 10
399 | RI | B-9 | IGC FAILURE | 2009-05-26 02:13 | 2009-05-26 11:25 | 9
421 | RI | U-2 | TRIPPED OFF LINE, GOV. PROBLEMS | 2009-07-27 18:40 | 2009-07-28 09:35 | 15
424 | RI | B-6 | GENERATOR TRIP ON HIGH PHASE OVER CURRENT SHORTLY AFTER START-UP. | 2009-08-10 18:23 | 2009-08-11 11:00 | 17
425 | RI | B-4 | CANNOT CLOSE FIELD BREAKER | 2009-08-10 19:06 | 2009-08-11 10:00 | 15
444 | RI | U-6 | DURING SLUICE TESTING UNIT WOULD NOT RESTORE, D.T.G. WOULD NOT OPEN OR CLOSE (STUCK AROUND 30%). INCOMPLETE SHUTDOWN WITH NO PRESTARTS. | 2009-09-23 10:35 | 2009-09-24 18:30 | 32
446 | RI | U-6 | WICKET GATE LOCKS WILL NOT RELEASE | 2009-09-24 00:24 | 2009-09-25 00:59 | 25
456 | RI | B-5 | UNIT WONT ROLL IGC PROBLEM | 2009-10-19 13:27 | 2009-10-21 13:59 | 49
460 | RI | U-7 | BROKEN SHEAR PIN | 2009-11-08 00:36 | 2009-11-08 13:30 | 13
461 | RI | U-7 | BROKEN SHEAR PIN ON SHUTDOWN | 2009-11-12 02:30 | 2009-11-12 08:58 | 6
462 | RI | U-8 | HEAT EXCHANGER LEAKING WATER | 2009-11-13 10:13 | 2009-11-28 12:45 | 363
484 | RI | U-1 | UNIT WOULD NOT SYNC | 2010-01-15 09:01 | 2010-01-28 18:49 | 322
488 | RI | B-1 | IGC PROBLEMS | 2010-01-22 10:55 | 2010-01-28 18:49 | 152
489 | RI | B-9 | BUS CLEARED TO ISOLATE UNIT, SHUT DOWN WITH NO GEN BRKR OPENING | 2010-01-22 15:17 | 2010-01-22 20:54 | 6
490 | RI | B-HU | FIELD BRKR WOULD NOT CLOSE | 2010-01-22 16:40 | 2010-01-22 21:44 | 5
524 | RI | U-8 | BREAKER CONTROL WIRING SMOKED AS BULB WAS REPLACED | 2010-03-26 19:04 | 2010-03-27 11:07 | 16
560 | RI | B-3 | WATER IN OIL IN THRUST POT | 2010-07-08 07:00 | 2010-07-09 16:38 | 34
565 | RI | B-3 | BAD UNIT VOLTAGE | 2010-07-12 16:47 | 2010-07-13 12:00 | 19
559 | RI | B-1 | AIR GAP INSPECTION & BRUSH REPAIRS | 2010-07-12 23:28 | 2010-07-16 16:40 | 89
567 | RI | U-2 | WILL NOT START DUE TO "RDR" LEVEL SWITCH B/O | 2010-07-15 19:34 | 2010-07-16 14:30 | 19
601 | RI | U-8 | BAD RTU BOARD | 2010-10-15 20:00 | 2010-10-16 10:55 | 15
609 | RI | U-4 | UNIT TRIPPED OFFLINE 51 VG SYSTEM FAULT B/U B PHASE FLAG TRIPPED ON U-4 | 2010-11-15 02:56 | 2010-11-15 10:52 | 8
618 | RI | U-2 | EXCITER PANEL SMOKED, CAUSED UNIT TO 86 OUT | 2010-11-27 12:37 | 2010-11-27 18:33 | 6
629 | RI | B-3 | IGC FAILURE CANT START | 2010-12-26 12:52 | 2010-12-27 15:31 | 27
632 | RI | B-9 | UNDER VOLTAGE TRIP | 2011-01-13 03:37 | 2011-01-14 13:07 | 34
636 | RI | B-9 | TRIPPED ON UNDER VOLTAGE | 2011-02-16 01:06 | 2011-02-16 09:57 | 9
639 | RI | B-9 | TRIPPED ON UNDERVOLTAGE | 2011-03-02 02:01 | 2011-03-02 08:57 | 7
641 | RI | B-10 | B-10 POWER MONITOR FAILURE | 2011-03-13 12:35 | 2011-03-14 15:05 | 27
663 | RI | U-6 | 86G LOCKOUT | 2011-06-28 11:00 | 2011-06-28 20:17 | 9
671 | RI | U-7 | ACCUM TANKS EMPTY | 2011-07-20 22:08 | 2011-07-24 13:21 | 87
675 | RI | U-2 | NO PRESTARTS/NO OIL INJECTION | 2011-09-16 08:34 | 2011-09-16 17:30 | 9
690 | RI | b-hu | NOT STARTING | 2011-10-07 15:05 | 2011-10-08 16:30 | 25
698 | RI | B-1 | UNIT SWINGING ON START-UP AND ON LINE | 2011-11-03 16:09 | 2011-11-05 14:15 | 46
706 | RI | B-8 | UNIT TRIPPED ON OVERVOLTAGE 16800 | 2011-12-04 20:39 | 2011-12-05 10:09 | 14
707 | RI | B-8 | UNIT TRIPPED ON OVERVOLTAGE | 2011-12-05 19:34 | 2011-12-06 12:03 | 16
709 | RI | U-1 | EXCITER TRANSFORMER TP13 INSULATION AND LEADS GLOWING - TRANSFORMER APPEARS B/O | 2011-12-07 22:07 | 2011-12-08 15:48 | 18
722 | RI | B-10 | RECIEVE SHEAR PIN FAILURE | 2012-02-12 21:25 | 2012-02-13 08:10 | 11
727 | RI | U-7 | SMALL FIRE IN DTG D.C. CONTROL OF U-7 | 2012-02-25 18:32 | 2012-02-27 16:22 | 46
728 | RI | U-7 | GOV. SYS. PROBLEMS | 2012-02-27 21:31 | 2012-02-28 08:00 | 10
731 | RI | B-10 | KEEPS TRYING TO RUN ON ISO-GRID MODE, WICKET GATE ALARMS, AND MCM CHANNEL 9 STATOR SOLE PLATE MOVEMENT ALARM | 2012-03-04 15:28 | 2012-03-05 10:57 | 19
740 | RI | U-2 | U-2 HAD HIGH THRUST BRG TEMP ALARM AND TRIPPED OFFLINE -NO HIGH TEMPS NOTED ON PIE OR VAX | 2012-04-27 16:50 | 2012-04-28 09:46 | 17
759 | RI | B-10 | POWER MONITOR COMM. MODULE FAULTY | 2012-06-22 03:00 | 2012-06-22 09:42 | 7
766 | RI | U-5 | GOVERNOR SYSTEM PROBLEMS | 2012-07-12 14:03 | 2012-07-13 14:59 | 25
771 | RI | B-9 | POWER MONITOR ALARM. UNIT BEING SHUTDOWN FOR MONITOR REPLACEMENT | 2012-07-30 10:23 | 2012-07-30 15:42 | 5
774 | RI | B-7 | 86 REVERSE POWER TRIP | 2012-08-12 20:55 | 2012-08-13 08:51 | 12
782 | RI | U-3 | LEAKING OIL | 2012-08-20 12:56 | 2012-08-28 14:23 | 193
788 | RI | B-1 | OVER SPEED AT START | 2012-08-30 12:58 | 2012-08-31 13:16 | 24
791 | RI | U-3 | 86 OPERATION, 5-6 AIR/OIL SEAL LOW LOW, 2-1 UPSTREAM GUIDE THRUST/COUNTER THRUST LOW OIL | 2012-09-09 23:45 | 2012-09-10 13:36 | 14
817 | RI | U-7 | COOLING WATER INTAKE PLUGGED - FOUND SLEEPING BAG, MATTRESS & PARTS OF A TENT CRAMMED IN THE INTAKE | 2012-11-19 15:21 | 2012-11-20 09:47 | 18
818 | RI | B-4 | UNIT TRIPS ON OVER/UNDER EXCITATION WHEN FIELD BRKR IS CLOSED | 2012-11-20 19:50 | 2012-11-21 07:07 | 11
819 | RI | B-2 | NO FIELD FLASHING - NO SPEED INDICATION | 2012-11-26 17:50 | 2012-11-27 09:02 | 15
821 | RI | B-9 | GEN. BRAKE #4 NOT RELEASING OR SWITCH | 2012-12-11 23:44 | 2012-12-12 12:05 | 12
G014296 | RI | B9 | power system monitor | 2013-01-17 13:38 | 2013-01-17 23:59 | 10
G014306 | RI | B9 | Govenor Control Problems | 2013-02-20 13:47 | 2013-02-21 23:59 | 34
G014374 | RI | U3 | Unintended technician trip | 2013-02-28 18:20 | 2013-02-28 23:59 | 6
G014375 | RI | U4 | Unitended technician trip | 2013-02-28 18:20 | 2013-02-28 23:59 | 6
G014376 | RI | U2 | 86 relay | 2013-02-28 18:41 | 2013-02-28 23:59 | 5
G014391 | RI | B9 | electronic power supply issue on Governor system. | 2013-03-08 07:53 | 2013-03-08 23:59 | 16
G014394 | RI | U3 | water in exciter cabinet | 2013-03-10 12:06 | 2013-03-12 23:59 | 60
G014402 | RI | U8 | High water in turbine compartment | 2013-03-18 06:40 | 2013-03-18 23:59 | 17
G014469 | RI | B9 | Unit will not load up after start-up. | 2013-04-27 09:27 | 2013-04-28 23:59 | 39
G014470 | RI | U7 | Gov oil pump | 2013-04-28 17:53 | 2013-04-29 23:59 | 30
G014471 | RI | U7 | Accumulator oil problems | 2013-04-29 06:55 | 2013-04-29 23:59 | 17
G014484 | RI | U7 | Will not start | 2013-05-02 14:39 | 2013-05-03 15:39 | 25
G014571 | RI | U2 | GOV, drawer repalced, no control power. | 2013-06-10 09:24 | 2013-06-10 23:59 | 15
G014573 | RI | B9 | Forced outage | 2013-06-11 06:17 | 2013-06-11 23:59 | 18
G014579 | RI | U8 | Tripped during testing | 2013-06-13 08:40 | 2013-06-13 23:59 | 15
G014580 | RI | U6 | Tripped during wireman testing | 2013-06-13 10:57 | 2013-06-13 23:59 | 13
G014661 | RI | U6 | Sheerpin failure indication | 2013-07-21 07:06 | 2013-07-22 23:59 | 41
G014664 | RI | U7 | Unloader valve repair | 2013-07-23 10:34 | 2013-07-24 06:00 | 19
G014670 | RI | B10 | investigating air gap issue | 2013-07-25 07:32 | 2013-07-26 23:59 | 40
G014673 | RI | U1 | U-1 and U-2 derated to 20 MWs due to cooling fan issues | 2013-07-25 18:11 | 2013-07-26 23:59 | 30
G014686 | RI | B1 | bad 86 lock-out switch | 2013-08-01 00:56 | 2013-08-01 23:59 | 23
G014790 | RI | U5 | Bus #2 Differential | 2013-09-12 16:41 | 2013-09-13 23:59 | 31
G014791 | RI | U6 | Bus #2 Differential | 2013-09-12 16:43 | 2013-09-13 23:59 | 31
G014792 | RI | U7 | Bus #2 Differential | 2013-09-12 16:46 | 2013-09-13 23:59 | 31
G014803 | RI | B6 | Not enough air gap during testing. | 2013-09-17 10:13 | 2013-12-31 23:59 | 2534
G014888 | RI | B9 | Tail water sensor failure | 2013-10-13 03:57 | 2013-10-14 23:59 | 44
G014912 | RI | B7 | tripped during startup. | 2013-10-18 10:05 | 2013-10-18 23:59 | 14
G014967 | RI | U7 | Air cool leak | 2013-11-12 11:14 | 2013-11-13 23:59 | 37
G015014 | RI | U7 | Gate lock stuck. | 2013-12-05 04:23 | 2013-12-05 23:59 | 20
G015117 | RI | U8 | Failed to start | 2013-12-22 03:58 | 2013-12-23 23:59 | 44
G015118 | RI | U2 | Failed to start | 2013-12-26 04:58 | 2013-12-26 23:59 | 19
G015121 | RI | B6 | IGC control failure. | 2014-01-02 01:23 | 2014-01-02 23:59 | 23
G015149 | RI | B6 | IGC Issues | 2014-01-28 01:12 | 2014-01-29 23:59 | 47
G015151 | RI | B6 | IGC Failure | 2014-01-28 14:49 | 2014-01-29 23:59 | 33
G015164 | RI | B9 | Brake issue | 2014-02-05 06:29 | 2014-02-05 23:59 | 17
G015173 | RI | B9 | Brake switch issues | 2014-02-10 01:42 | 2014-02-10 23:59 | 22
G015182 | RI | B6 | Problems with 86 relay | 2014-02-12 12:02 | 2014-02-13 23:59 | 36
G015211 | RI | B5 | Head cover issues. | 2014-02-27 18:00 | 2014-03-31 18:00 | 768
G015212 | RI | B6 | Head cover issues | 2014-02-27 18:00 | 2014-03-31 18:00 | 768
G015213 | RI | B7 | Head cover issues | 2014-02-27 18:00 | 2014-03-31 18:00 | 768
G015214 | RI | B8 | Head cover issues | 2014-02-27 18:00 | 2014-03-31 18:00 | 768
G015218 | RI | B9 | B-9 tripped off line due to the loss of the tailwater indication | 2014-03-01 15:51 | 2014-03-02 23:59 | 32
G015219 | RI | B7 | Unstable due to Wanapum pool drawdown. | 2014-03-02 02:30 | 2014-03-31 01:20 | 695
G015220 | RI | B6 | Unstable due to Wanapum pool drawdown. | 2014-03-02 02:30 | 2014-03-31 01:21 | 695
G015221 | RI | B5 | Unstable due to Wanapum pool drawdown. | 2014-03-02 02:30 | 2014-03-31 01:22 | 695
G015222 | RI | B4 | Governor unable to control and vibration. Wanapum pool drawdown | 2014-03-02 02:30 | 2014-03-31 01:22 | 695
G015223 | RI | B3 | Governor unable to control and vibration. Wanapum pool drawdown | 2014-03-02 02:30 | 2014-03-31 01:24 | 695
G015230 | RI | U2 | Unavailable due tailwater dropping below 558 feet while Wanapum is lowering headwater for repairs. | 2014-03-03 01:48 | 2014-03-07 23:59 | 118
G015231 | RI | U3 | Unavailable due tailwater dropping below 558 feet while Wanapum is lowering headwater for repairs. | 2014-03-03 01:48 | 2014-03-07 23:59 | 118
G015232 | RI | U4 | Unavailable due tailwater dropping below 558 feet while Wanapum is lowering headwater for repairs. | 2014-03-03 01:48 | 2014-03-07 23:59 | 118
G015233 | RI | U5 | Unavailable due tailwater dropping below 558 feet while Wanapum is lowering headwater for repairs. | 2014-03-03 01:48 | 2014-03-07 23:59 | 118
G015234 | RI | U6 | Unavailable due tailwater dropping below 558 feet while Wanapum is lowering headwater for repairs. | 2014-03-03 01:48 | 2014-03-07 23:59 | 118
G015235 | RI | U7 | Unavailable due tailwater dropping below 558 feet while Wanapum is lowering headwater for repairs. | 2014-03-03 01:48 | 2014-03-07 23:59 | 118
G015236 | RI | U8 | Unavailable due tailwater dropping below 558 feet while Wanapum is lowering headwater for repairs. | 2014-03-03 01:48 | 2014-03-07 23:59 | 118
G015237 | RI | RIPH1Plant | Powerhouse 1 declared unavailable due to gross head exceeding limits while assisting Wanapum Dam in meeting headwater requirements for repairs. | 2014-03-03 17:12 | 2014-03-10 23:59 | 175
G015265 | RI | B3 | Investigate cause of water in the oil system. | 2014-03-17 14:54 | 2014-03-21 17:50 | 99
G015285 | RI | B9 | Unknown issue. | 2014-03-20 21:44 | 2014-03-21 23:59 | 26
G015330 | RI | B6 | Generator control computer issues | 2014-04-08 14:15 | 2014-04-09 23:59 | 34
G015482 | RI | B06 | Minimum air gap has been reached. | 2014-05-29 15:39 | 2016-05-16 07:10 | 17224
G015491 | RI | B1 | Tripped offline due to high exciter temperature. | 2014-06-02 12:59 | 2014-06-03 23:59 | 35
G015493 | RI | B9 | High exciter temperature. | 2014-06-03 14:25 | 2014-06-04 23:59 | 34
G015511 | RI | B10 | unknown , troubleshooting | 2014-06-10 04:37 | 2014-06-10 23:59 | 19
G015633 | RI | B09 | Has a communication problem. | 2014-07-18 14:45 | 2014-07-19 16:55 | 26
G015634 | RI | B07 | Sight glass oil leak | 2014-07-20 07:33 | 2014-07-21 23:59 | 40
G015661 | RI | B08 | Forced out by Chief due to air gap indication low. | 2014-08-04 23:10 | 2014-08-05 07:17 | 8
G015676 | RI | B09 | Thrust bearing problems. | 2014-08-09 06:46 | 2014-08-09 11:17 | 5
G015679 | RI | B08 | Tripped on air gap alarm. | 2014-08-10 14:23 | 2014-08-19 16:00 | 218
G015712 | RI | U05 | Unit will not start, investigating | 2014-08-21 14:53 | 2014-08-22 10:44 | 20
G015741 | RI | B10 | Failed to start due to failed relay. | 2014-09-03 09:31 | 2014-09-03 14:14 | 5
G015764 | RI | U01 | Bad network switch | 2014-09-14 15:09 | 2014-09-15 14:19 | 23
G015781 | RI | B08 | Govenor Oil Pump failure. Further investigation required No ETR at this time. | 2014-09-23 15:50 | 2014-09-24 10:33 | 19
G015815 | RI | B10 | Generator guide brg high temp | 2014-10-06 21:09 | 2014-10-07 15:54 | 19
G015823 | RI | B09 | Rotor Ground | 2014-10-10 07:40 | 2014-10-10 14:33 | 7
G015825 | RI | B09 | Exciter problems | 2014-10-12 20:23 | 2014-10-15 23:59 | 76
G015859 | RI | B09 | 2 Rotor ground alarms, investigation has reveled an exciter problem. | 2014-10-27 10:12 | 2014-10-31 09:56 | 96
G015983 | RI | B04 | Failure to Start, RTD failed, changed element. | 2014-11-15 18:13 | 2014-11-16 09:04 | 15
G016113 | RI | U03 | Draft Tube Gate Testing (problem with testing today [1/30/15].) | 2015-02-02 11:10 | 2015-02-02 15:50 | 5
G016467 | RI | U08 | Keeps tripping off lin. | 2015-03-09 17:19 | 2015-03-10 07:10 | 14
G016524 | RI | U05 | Nut found on floor beside unit from wicket gate linkage. | 2015-04-08 16:06 | 2015-04-09 09:12 | 17
G016566 | RI | B01 | Brake is stuck in the on position | 2015-04-26 14:38 | 2015-04-27 10:04 | 19
G016632 | RI | B08 | B8-declared unavailable to isolate bus for Station Service | 2015-05-21 19:10 | 2015-05-22 05:00 | 10
G016633 | RI | U06 | Issues with a solenoid valve. troubleshooting in progress | 2015-05-22 14:14 | 2015-05-22 23:59 | 10
G016669 | RI | B01 | B-1 Failed to start | 2015-06-05 16:35 | 2015-06-08 11:10 | 67
G016707 | RI | U05 | This is a reduction from 54MVA to 50MVA because 1 cooling fan is out of service. | 2015-06-22 09:22 | 2015-09-11 10:12 | 1945
G016964 | RI | U06 | Oil leak | 2015-09-01 08:12 | 2015-10-24 15:45 | 1280 | 0
G017000 | RI | U02 | Wiring changes for U3 Gov work require U1 & U2 out for 4 hours. | 2015-09-09 07:40 | 2015-09-09 13:45 | 6
G016999 | RI | U01 | Wiring changes for U3 Gov work requires U1 & U2 for 4 hours. | 2015-09-09 07:40 | 2015-09-09 13:45 | 6
G017112 | RI | U07 | Generator cooler leak | 2015-09-26 14:11 | 2015-10-01 11:39 | 117
G017195 | RI | U05 | Wicket gate issues. Operator investigating. | 2015-10-16 06:49 | 2015-10-16 17:58 | 11
G017257 | RI | B09 | Vibration issues, unit is restricted to a operating range of 10MW to 18MW | 2015-11-02 07:30 | 2015-12-10 09:45 | 914 | 18
G017258 | RI | B10 | Vibration issues, unit is restricted to a operating range of 8MW to 18MW | 2015-11-02 07:37 | 2015-12-10 09:45 | 914 | 18
G017301 | RI | B07 | 2015-2017 OUTAGE PRIOR TO MODERNIZATION | 11/16/2015 13:39 | 10/13/2016 12:50 | 7967.1833
G017369 | RI | B08 | Brush Maint. | 2015-11-19 21:00 | 2015-11-20 06:00 | 9
G017384 | RI | U02 | sheard pin during shutdown | 2015-12-16 02:12 | 2015-12-16 08:24 | 6
G017459 | RI | RIPH2 Plant | This derate is support the work on the RI2-Val line. This line is already out of service, but with the untis coming back due to changing the diving plan we need to derate the plant to ensure we don't overload the RI2-McK line. | 01/12/2016 14:30 | 01/14/2016 15:45 | 49.25
G017480 | RI | B05 | broken pins on wicket gates | 2016-01-14 17:09 | 2016-02-15 15:19 | 766
G017460 | RI | U05 | Contractor diving at night - outages w/be 1/14, 1/16 and 1/17/16 from 18:10 to 04:50 each night. Diving for denil removal and ground mat repairs | 2016-01-14 18:13 | 2016-01-18 02:11 | 80
G017461 | RI | U06 | Contractor diving at night - outages w/be 1/14, 1/16 and 1/17/16 from 18:10 to 04:50 each night. Diving for denil removal and ground mat repairs | 2016-01-14 18:13 | 2016-01-18 02:11 | 80
G017506 | RI | U05 | Gate lock malfunction | 2016-01-24 14:27 | 2016-01-25 08:04 | 18
G017539 | RI | U05 | The initial gate lock problem has uncovered a more significant problem with the servo linkage pin. | 02/10/2016 07:10 | 02/15/2016 15:15 | 128.0833
G017566 | RI | B05 | Wicket gate problem. | 2016-02-16 18:52 | 2016-02-17 11:10 | 16
G017573 | RI | U03 | Trunion oil leak | 2016-02-18 14:48 | 2016-03-03 08:50 | 330
G017710 | RI | B05 | Diving on B6 head gates, divers want B5 out while in north slot. | 2016-04-14 07:10 | 2016-04-14 12:25 | 5
G017743 | RI | U08 | High Trash rack differentials | 2016-04-15 09:16 | 2016-04-15 14:25 | 5 | 40
G017745 | RI | B08 | Brush replacement. | 2016-04-15 22:15 | 2016-04-16 07:00 | 9
G017752 | RI | B05 | Diving on B6, installing de-watering pumps | 04/25/2016 07:20 | 04/25/2016 13:30 | 6.1667
G017753 | RI | B08 | Diving on B6, installing de-watering pumps | 04/25/2016 07:20 | 04/25/2016 13:30 | 6.1667
G017754 | RI | B09 | Diving on B6, installing de-watering pumps | 04/25/2016 07:20 | 04/25/2016 13:30 | 6.1667
G017755 | RI | B05 | Diving on B6, installing de-watering pumps | 04/26/2016 07:10 | 04/26/2016 12:30 | 5.3333
G017756 | RI | B08 | Diving on B6, installing de-watering pumps | 04/26/2016 07:10 | 04/26/2016 12:30 | 5.3333
G017757 | RI | B09 | Diving on B6, installing de-watering pumps | 04/26/2016 07:10 | 04/26/2016 12:30 | 5.3333
G017787 | RI | RIPH2 Plant | Unit U-1 and U-3 derated to 44 mws due to cavitation. Unit U-8 derated to 42.5 mws due to cavitation and trash rack alarms. | 2016-05-06 00:10 | 2016-05-10 07:50 | 104 | 321
G017983 | RI | U04 | Water in the bulb | 2016-07-09 19:42 | 2016-07-10 12:33 | 17
G018024 | RI | U04 | U-4 gate distributing valve investigation | 07/26/2016 07:42 | 07/26/2016 13:00 | 5.3
G018158 | RI | B01 | BO1 FORCED OUTAGE - BLADE INSPECTIONS prior to MB 2016-2019 OUTAGE | 02/08/2016 12:23 | 04/08/2016 15:50 | 1443.45
G018208 | RI | U06 | Replace transformer bushing. | 2016-09-30 12:54 | 2016-10-21 17:15 | 508
G018350 | RI | U06 | Breaker will not close. | 2016-11-06 06:09 | 2016-11-06 11:57 | 6
G018517 | RI | U03 | U3 has a cracked governor oil pipe that needs to be repaired | 01/19/2017 06:15 | 01/19/2017 15:38 | 9.3833
G018582 | RI | B09 | Technician testing speed switch. | 01/27/2017 08:16 | 01/27/2017 14:39 | 6.3833
G018591 | RI | U08 | Trunion Seal oil Leak | 01/27/2017 12:25 | 02/05/2017 17:55 | 221.5
G018628 | RI | U08 | Oil line cracked. | 02/14/2017 07:12 | 02/14/2017 16:05 | 8.8833
G018645 | RI | B08 | Retrieve head gate stancion. | 02/15/2017 10:50 | 02/16/2017 13:08 | 26.3
17-07252 | RI | B09 | Blade deviation, need to replace card in gov. | 04/13/2017 08:17 | 04/13/2017 15:41 | 7.4
17-07372 | RI | U05 | Investigate comms/controls issues. | 05/17/2017 12:07 | 05/17/2017 20:00 | 7.8833
17-07408 | RI | B09 | troubleshooting | 2017-05-27 12:09 | 05/30/2017 08:31 | 68.3667
17-07450 | RI | B09 | troubleshooting | 2017-06-10 21:09 | 2017-06-12 13:55 | 40.7667
17-07490 | RI | U04 | Repair switch | 06/20/2017 22:05 | 06/21/2017 05:05 | 7
17-07558 | RI | B08 | Trunnion Seals issues | 07/17/2017 08:54 | 07/24/2017 07:10 | 166.2667
17-07597 | RI | RIPH1Plant | Rock Island ICCP link out of service. Engineers troubleshooting | 07/28/2017 04:26 | 07/28/2017 10:47 | 6.35
17-07610 | RI | B07 | 2017 FORCED OUTAGE PRIOR TO B07 MODERNIZATION | 08/02/2017 14:33 | 12/11/2017 07:10 | 3136.6167
17-07620 | RI | U04 | U04 TRANSDUCER CALIBRATION | 08/08/2017 07:10 | 08/08/2017 13:18 | 6.1333
17-07639 | RI | U03 | repair blade distributing valve | 08/12/2017 11:51 | 08/14/2017 10:54 | 47.05
17-07675 | RI | U06 | Investigation of CO2 discharge | 08/24/2017 16:07 | 08/28/2017 13:31 | 93.4
17-07936 | RI | B08 | Exciter alarms while trying to startup after scheduled outage | 12/01/2017 16:49 | 12/04/2017 16:18 | 71.4833
17-07950 | RI | B08 | Oil leaking to be investigated Friday morning. Plant engineer requests unit down overnight. | 12/14/2017 20:00 | 12/15/2017 08:45 | 12.75
1-00350097 | RI | B03 | 2016-2019 OUTAGE PRIOR TO MODERNIZATION | 05/28/2018 06:10 | 04/08/2016 05:51 | 18720.3167
1-00506761 | RI | B04 | 2016-2018 OUTAGE PRIOR TO 2018 MODERNIZATION on G013494 This outage replaces G017544 per Peak RC's Request | 04/19/2018 07:10 | 04/08/2016 07:10 | 17784
1-00612702 | RI | B05 | Troubleshooting | 11/23/2018 16:00 | 11/18/2018 19:08 | 116.8667
| RI | B05 | oil in tailrace | 03/30/2018 23:59 | 03/29/2018 17:13 | 30.7667
1-00606876 | RI | B05 | Investigate and repair MW output discrepancies. | 10/23/2018 23:59 | 10/22/2018 06:54 | 41.0833
1-00608085 | RI | B05 | trouble voltage regulator | 11/02/2018 23:59 | 10/26/2018 19:32 | 172.45
1-00615101 | RI | B05 | Investigate oil leak | 12/17/2018 07:10 | 11/30/2018 13:30 | 401.6667
1-00570515 | RI | B06 | troubleshooting | 05/18/2018 23:59 | 05/17/2018 20:25 | 27.5667
| RI | B06 | troubleshoot and repair | 05/12/2018 23:59 | 05/11/2018 02:04 | 45.9167
1-00577349 | RI | B06 | Troubleshoot exciter alarm. | 06/25/2018 23:59 | 06/15/2018 07:23 | 256.6
| RI | B06 | Troubleshoot. | 08/06/2018 23:59 | 08/04/2018 08:17 | 63.7
1-00593581 | RI | B06 | Smoke investigation | 11/02/2018 15:50 | 08/22/2018 22:02 | 1721.8
1-00608463 | RI | B06 | Trouble shoot low oil in the thrust pot. | 10/30/2018 23:59 | 10/29/2018 18:14 | 29.75
1-00609785 | RI | B06 | Generator Breaker keeps opening. | 11/07/2018 23:59 | 11/04/2018 05:50 | 90.15
1-00533270 | RI | B07 | B07 FORCED OUTAGE PRIOR TO MODERNIZATION This outage follows 17-07610 which began 8/2/2017 and ended 12/11/17. Work on this unit scheduled to begin March 12, 2018 | 03/19/2018 07:10 | 12/11/2017 07:10 | 2352
| RI | B08 | Brush maintenance | 02/11/2018 23:59 | 02/10/2018 20:14 | 27.75
1-00556842 | RI | B08 | During today's routine maintenance found some other issues | 03/20/2018 13:50 | 03/19/2018 13:50 | 24
1-00557269 | RI | B08 | B08 TURBINE HUB INVESTIGATION | 04/26/2018 17:50 | 03/20/2018 13:50 | 892
| RI | B08 | mitigate unplanned shut down and damage due to lightning activity in the area. | 05/24/2018 23:59 | 05/23/2018 19:10 | 28.8167
| RI | B08 | Repair | 07/16/2018 23:59 | 07/15/2018 10:41 | 37.3
| RI | B08 | repair | 07/18/2018 23:59 | 07/17/2018 05:30 | 42.4833
1-00508938 | RI | B09 | B09 TROUBLESHOOTING UNIT TRIP This outage Replaces 17-07481 and COS 1-00490089 (Completed prematurely in COS) | 10/03/2018 23:59 | 06/16/2017 07:10 | 11392.8167
| RI | B10 | trouble shoot oil leak | 03/30/2018 23:59 | 03/29/2018 17:03 | 30.9333
| RI | B10 | Shut down for lightning storm in the area to mitigate unplanned shutdown. | 05/24/2018 23:59 | 05/23/2018 18:10 | 29.8167
| RI | B10 | troubleshoot noise in B-10 exciter | 06/01/2018 17:50 | 06/01/2018 10:37 | 7.2167
1-00553925 | RI | U01 | Troubleshoot CO2 discharge | 03/07/2018 23:59 | 03/05/2018 18:20 | 53.65
1-00570518 | RI | U01 | Troubleshooting | 05/18/2018 23:59 | 05/17/2018 19:59 | 28
1-00611206 | RI | U01 | extended outage TOA G013723 (COS 1-00583593), U01 2018 OVERHAUL, DTG | 11/13/2018 17:50 | 11/09/2018 17:50 | 96
1-00614296 | RI | U02 | Repairs to gate lock. It will not release. | 11/28/2018 23:59 | 11/28/2018 06:31 | 17.4667
1-00562688 | RI | U03 | Troubleshoot unit trip | 04/12/2018 23:59 | 04/11/2018 21:19 | 26.6667
1-00570516 | RI | U03 | troubleshooting | 05/18/2018 23:59 | 05/17/2018 19:00 | 28.9833
| RI | U03 | Testing for exciter trouble | 03/14/2018 23:59 | 03/13/2018 22:45 | 25.2333
1-00573528 | RI | U03 | Sheer Pin Failure | 06/02/2018 23:59 | 06/01/2018 09:44 | 38.25
1-00577655 | RI | U03 | replace shear pin | 06/17/2018 23:59 | 06/16/2018 19:45 | 28.2333
1-00583344 | RI | U03 | Troubleshoot exciter | 07/16/2018 16:00 | 07/14/2018 03:30 | 60.5
| RI | U03 | Repair bearing indications | 08/09/2018 23:59 | 08/08/2018 14:12 | 33.7833
1-00586133 | RI | U05 | Investigate Alarm. | 07/30/2018 23:59 | 07/28/2018 19:08 | 52.85
| RI | U05 | investigation | 09/11/2018 23:59 | 09/10/2018 05:35 | 42.4
1-00557833 | RI | U06 | Unable to get the fans running. This is a forced outage that starts when the planned outage was supposed to end | 03/28/2018 17:50 | 03/23/2018 17:50 | 120
1-00550420 | RI | U07 | troubleshoot loss of lube oil pumps | 02/22/2018 23:59 | 02/22/2018 06:54 | 17.0833
1-00566343 | RI | U07 | Troubleshoot unit trip | 05/02/2018 23:59 | 05/01/2018 16:06 | 31.8833
1-00620652 | RI | U07 | Troubleshoot and repair governor problem | 12/28/2018 23:59 | 12/27/2018 02:27 | 45.5333
1-00562561 | RI | U07 | Unit tripped during a software upload. | 04/12/2018 23:59 | 04/11/2018 09:34 | 38.4167
1-00562797 | RI | U07 | Forced outage, unit locked out on 86 | 04/13/2018 23:59 | 04/12/2018 10:50 | 37.15
| RI | U07 | emergency trip, cause unknown | 05/11/2018 23:59 | 05/10/2018 04:25 | 43.5667
1-00572966 | RI | U07 | Troubleshoot unit | 05/31/2018 23:59 | 05/30/2018 10:57 | 37.0333
1-00617847 | RI | U07 | Unit needs to be reset locally. Tripped offline due to exciter problem. | 12/16/2018 23:59 | 12/15/2018 20:27 | 27.5333
1-00545957 | RI | U08 | Clean trash racks | 02/02/2018 23:59 | 02/02/2018 07:42 | 16.2833
1-00547277 | RI | U08 | Trash rack cleaning | 02/08/2018 18:00 | 02/08/2018 11:10 | 6.8333
| RI | B05 | 7053 - Governor Oil System | 2019-01-01 | 2019-03-13 07:10 | 1711.1667
| RI | B07 | 4830 - Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 2019-01-01 | 2019-03-19 07:00 | 1855
| RI | B10 | 4550 - Generator bearings and lube oil system (including thrust bearings on hydro units) | 2019-01-14 16:47 | 2019-03-04 17:50 | 1177.05
| RI | B08 | 4840 - Inspection E | 2019-02-20 20:20 | 2019-02-21 14:55 | 18.5833
| RI | U08 | 4620 - Air cooling system | 2019-03-15 07:10 | 2019-03-15 14:37 | 7.45
| RI | U01 | 4620 - Air cooling system | 2019-03-20 07:10 | 2019-03-20 15:51 | 8.6833
| RI | U02 | 4620 - Air cooling system | 2019-03-21 07:10 | 2019-03-21 15:02 | 7.8667
| RI | B09 | 4750 - Other generator controls and metering problems | 2019-03-28 02:11 | 2019-03-28 11:12 | 9.0167
| RI | U03 | 4605 - Exciter transformer | 2019-05-20 19:03 | 2019-05-21 13:08 | 18.0833
| RI | B09 | 4609 - Other exciter problems | 2019-06-15 08:55 | 2019-06-17 10:07 | 49.2
| RI | U06 | 4605 - Exciter transformer | 2019-06-24 03:07 | 2019-06-25 23:59 | 44.8667
| RI | B06 | 7001 - Shaft packing | 2019-07-26 11:57 | 2019-08-23 15:59 | 676.0333
| RI | B06 | 7190 - Dewatering and rewatering equipment | 2019-11-25 06:05 | 2019-11-25 15:38 | 9.55
| RI | B08 | 7190 - Dewatering and rewatering equipment | 2019-11-25 07:12 | 2019-11-25 15:39 | 8.45
| RI | U06 | 7099 - Other turbine problems | 2019-12-23 20:10 | 2019-12-24 09:19 | 13.15
| RI | U06 | 7099 - Other turbine problems | 2019-12-24 09:46 | 2019-12-30 11:10 | 145.4
| RI | U05 | 7053 - Governor Oil System | 2020-02-17 19:39 | 2020-02-18 11:25 | 15.7667
| RI | B09 | 4550 - Generator bearings and lube oil system (including thrust bearings on hydro units) | 2020-03-02 03:35 | 2020-03-02 11:14 | 7.65
| RI | U03 | 7142 - Wicket gate shear pin | 2020-03-10 02:55 | 2020-03-10 08:59 | 6.0667
| RI | B04 | 9015 - Pandemic | 2020-03-23 15:30 | 2020-04-30 06:00 | 902.5
| RI | B05 | 9015 - Pandemic | 2020-03-23 15:30 | 2020-04-30 06:00 | 902.5
| RI | B07 | 9015 - Pandemic | 2020-03-23 15:30 | 2020-04-30 06:00 | 902.5
| RI | B10 | 9015 - Pandemic | 2020-03-23 15:30 | 2020-04-30 06:00 | 902.5
| RI | U06 | 7099 - Other turbine problems | 2020-03-25 21:44 | 2020-03-26 09:43 | 11.9833
| RI | U06 | 4620 - Air cooling system | 2020-04-16 13:27 | 2020-04-17 13:27 | 24
| RI | U06 | 7099 - Other turbine problems | 2020-05-21 20:13 | 2020-05-22 07:38 | 11.4167
| RI | U06 | 7099 - Other turbine problems | 2020-05-26 07:07 | 2020-05-29 09:32 | 74.4167
| RI | U02 | 7142 - Wicket gate shear pin | 2020-07-11 06:52 | 2020-07-11 15:56 | 9.0667
| RI | B06 | 7141 - Wicket gate operating mechanism or positioner | 2020-07-17 07:28 | 2020-07-17 14:26 | 6.9667
| RI | U02 | 7053 - Governor Oil System | 2020-08-02 11:12 | 2020-08-03 01:05 | 13.8833
| RI | B08 | 4609 - Other exciter problems | 2020-08-10 14:52 | 2020-08-12 16:19 | 49.45
| RI | B08 | 7053 - Governor Oil System | 2020-11-12 23:55 | 2020-11-13 09:48 | 9.8833
| RI | U01 | 7142 - Wicket gate shear pin | 2020-12-23 22:27 | 2020-12-24 08:42 | 10.25