## Sheet1
Equipment Size (Cooling Capacity:BTU/H) | Mode | Sub-Category or Rating conditoin | Efficiency Requirement
< 65,000 | Cooling | Split System and Sigle Package | 15.0 SEER
| Heating | Split System | 8.5 HSPF
Single Package
≥ 65,000 and < 135,000 | Cooling | Split System and Sigle Package | 12.4 IEER
| Heating | 47°F /43°F wb Outdoor Air | 3.4 COP
|  | 17°F db/ 15°F wb Outdoor Air | 2.3 COP
≥135,000 | Cooling | Split System and Sigle Package | 11.6 IEER
| Heating | 47°F /43°F wb Outdoor Air | 3.3 COP
|  | 17°F db/ 15°F wb Outdoor Air | 2.25 COP