## Sheet1
Equipment Size (Cooling Capacity:BTU/H) | Mode | Sub-Category or Rating conditoin | Efficiency Requirement
< 65,000 | Cooling | Split System and Sigle Package | 16.0 SEER
| Heating | Split System | 9.0 HSPF
|  | Single Package | 8.8 HSPF
≥ 65,000 and < 135,000 | Cooling | Split System and Sigle Package | 14.0 IEER
| Heating | 47°F /43°F wb Outdoor Air | 3.5 COP
|  | 17°F db/ 15°F wb Outdoor Air | 2.4 COP
≥135,000 | Cooling | Split System and Sigle Package | 12.5 IEER
| Heating | 47°F /43°F wb Outdoor Air | 3.4 COP
|  | 17°F db/ 15°F wb Outdoor Air | 2.4 COP