## Sheet1
Air-Source Heat Pumps 2024
Equipment Size (Cooling Capacity:BTU/H) | Mode | Sub-Category or Rating Condition | Efficiency Requirement | Efficiency Requirement 2
< 65,000 | Heating | Split System | 9.6 HSPF | 8.1 HSPF2
| Heating | Single Package | 8.3 HSPF | 7.0 HSPF2
≥ 65,000 and < 135,000 | Heating | 47°F /43°F wb Outdoor Air | 3.5 COP
≥135,000 | Heating | 47°F /43°F wb Outdoor Air | 3.4 COP
≥240,000 | Heating | 47°F /43°F wb Outdoor Air | 3.4 COP