## Disclaimer
Disclaimer of completeness and accuracy of data provided to evaluate slice product
The information contained in this spreadsheet or report was queried from a database. Chelan PUD disclaims any warranty or representation that this information is completely accurate. Individual entries in the database may contain inaccuracies that could be reflected in this information. If you have any questions, please call Janet Jaspers: janet.jaspers@chelanpud.org or Mike Bradshaw: mike.bradshaw@chelanpud.org

## Rocky Reach
Rocky Reach Forced (unplanned) outages
> 5 hour duration
Jan 1, 2006 through Dec 31, 2020
ID | Hydro | Unit | Reason | Date Off | Date On | Duration Hours | Derating
38 | RR | C-2 | EXCITER TROUBLE | 2006-01-09 05:25 | 2006-01-09 15:10 | 10
97 | RR | C-5 | UNIT FAILING TO START | 2006-11-08 08:14 | 2006-11-08 15:07 | 7
111 | RR | C-4 | SOFTWARE TIMEOUT ON STARTUP | 2006-12-30 06:11 | 2006-12-30 17:01 | 11
113 | RR | C-4 | 86M, BATTERY GROUNDS, START TIMOUT | 2007-01-04 05:22 | 2007-01-04 11:58 | 7
127 | RR | C-8 | GOVERNOR CPU FAILURE | 2007-03-04 05:30 | 2007-03-04 12:24 | 7
181 | RR | C-2 | GEN GUIDE BRG HI VIBRATION Y-AXIS | 2007-09-13 16:52 | 2007-09-14 18:04 | 25
185 | RR | C-3 | GENERATOR GUIDE BEARING TEMP HIHI/86M LOCKOUT RELAY TRIP | 2007-10-04 01:10 | 2007-10-04 08:16 | 7
201 | RR | C-10 | C-10 UNIT NOT IN PRESTART CONDITION AFTER SHUTDOWN | 2007-12-13 23:35 | 2007-12-14 06:42 | 7
258 | RR | C-11 | OIL SEAL LEAK IN C-11 ACB ENCLOSURE | 2008-08-23 15:25 | 2008-08-30 08:57 | 162
267 | RR | C-4 | EXCITER TROUBLE 86G GENERATOR LOCKOUT TRIP | 2008-09-23 18:58 | 2008-09-24 16:01 | 21
281 | RR | C-3 | 86-M WICKET GATE DEVIATING FROM SETPOINT | 2008-11-04 17:55 | 2008-11-05 03:32 | 10
351 | RR | C-2 | BAD SVE ON GATE SERVO, CAN'T GET IT TO SMOOTH OUT | 2009-02-10 09:11 | 2009-02-10 14:54 | 6
370 | RR | C-2 | BLADE CONTROL ISSUES | 2009-03-09 07:52 | 2009-03-09 13:19 | 5
395 | RR | C-2 | RUNNER BLADE VIBRATION | 2009-05-20 05:55 | 2009-05-20 14:46 | 9
423 | RR | C-5 | GENERATOR PHASE A-B, B-C AND C-A VOLTAGE LOW IN ALARM(ALL PHASE VOLTAGES READING 6.2KV AT TIME THE UNIT WAS STOPPED) | 2009-07-30 01:29 | 2009-07-30 09:49 | 8
426 | RR | C-10 | 86T TRIP LOCKOUT | 2009-08-11 02:05 | 2009-08-11 08:48 | 7
427 | RR | C-11 | 86T TRIP LOCKOUT | 2009-08-11 02:06 | 2009-08-11 08:48 | 7
428 | RR | C-6 | GEN PHASE VOLTAGES LOW | 2009-08-13 01:52 | 2009-08-13 08:12 | 6
557 | RR | C-9 | C-9 TURBINE PIT SUMP FLOATS NORMAL AND EMERGENCY FLOATS FAILED TO OPERATE, HIGH WATER LEVEL LEAKING WATER INTO TURBINE GUIDE BEARING OIL | 2010-07-04 01:19 | 2010-07-04 08:59 | 8
572 | RR | C-11 | 86G LOCKOUT RELAY TRIP/DGP RELAY B PHASE DIFFERENTIAL | 2010-08-25 09:04 | 2010-08-27 18:32 | 57
739 | RR | C-6 | ROTOR INSPECTION REASON: MO | 2012-04-20 04:02 | 2012-04-20 19:51 | 16
770 | RR | C-6 | 86M L.O. OPERATED | 2012-07-29 12:11 | 2012-07-29 20:28 | 8
776 | RR | C-5 | 86T RELAY OPERATION/U-1 | 2012-08-13 16:12 | 2012-08-14 14:54 | 23
816 | RR | C-8 | 86G TRIP | 2012-11-16 17:09 | 2012-11-16 23:31 | 6
G014328 | RR | C8 | ARC Net Comm Failure | 2013-02-04 04:56 | 2013-02-05 23:59 | 43
G014338 | RR | C7 | Turbine Guide bearing bad level sensing device | 2013-02-06 13:02 | 2013-02-07 23:59 | 35
G014408 | RR | C10 | Tripped offline | 2013-03-25 21:29 | 2013-03-26 23:59 | 26
G014410 | RR | C10 | Investigation of blade-gate timing relationship | 2013-03-26 08:50 | 2014-04-17 04:50 | 9284
G014473 | RR | C3 | Quide bearing oil level transducer problem. | 2013-04-29 14:40 | 2013-04-29 23:59 | 9
G014638 | RR | C1 | Clean Trash Racks. High differentials | 2013-07-12 03:10 | 2013-07-12 08:50 | 6
G014639 | RR | C2 | Clean Trash Racks. High Differentials | 2013-07-12 03:10 | 2013-07-12 08:50 | 6
G014640 | RR | C3 | Clean Trash Racks. High Differentials | 2013-07-12 03:10 | 2013-07-12 08:50 | 6
G014698 | RR | C1 | High trash rack differential. | 2013-08-07 13:15 | 2013-08-08 03:10 | 14
G014699 | RR | C1, C2, C3 | Clamming and diving on trash racks This derate (940 MW) does NOT include C-10. | 2013-08-08 03:10 | 2013-08-08 09:50 | 7
G014701 | RR | C1 | High Trashrack Differential | 2013-08-08 13:35 | 2013-08-11 23:59 | 82
G014732 | RR | C2 | Unit tripped on a blade deviation | 2013-08-18 02:27 | 2013-08-19 23:59 | 46
G014817 | RR | C8 | Investigating turbine servo rod condition | 2013-09-23 19:00 | 2014-02-14 06:50 | 3444
G014818 | RR | C9 | Investigating turbine servo rod condition | 2013-09-23 19:00 | 2014-01-20 06:50 | 2844
G014819 | RR | C11 | Investigating turbine servo rod condition | 2013-09-23 19:00 | 2013-12-27 08:00 | 2269
G014913 | RR | C4 | Tripped out | 2013-10-17 01:19 | 2013-10-18 23:59 | 47
G014931 | RR | C2 | Unit will not Sync | 2013-10-26 07:14 | 2013-10-26 23:59 | 17
G014961 | RR | C4 | Tripped during startup | 2013-11-07 03:18 | 2013-11-07 23:59 | 21
G014976 | RR | C4 | C-4 to unavailable on start-up. Software timeout | 2013-11-16 03:58 | 2013-11-18 23:59 | 68
G014985 | RR | C2 | Forced out due to headgate issues. | 2013-11-24 17:50 | 2013-11-25 23:59 | 30
G014992 | RR | C7 | Exciter trouble. | 2013-12-01 16:50 | 2013-12-02 23:59 | 31
G015116 | RR | C7 | Exciter problem | 2013-12-21 04:23 | 2013-12-21 23:59 | 20
G015146 | RR | C6 | 86 Relay | 2014-01-24 14:43 | 2014-01-24 23:59 | 9
G015160 | RR | C11 | Locked out on start-up | 2014-02-03 06:13 | 2014-02-04 23:59 | 42
G015193 | RR | C4 | Tripped to lockout on startup | 2014-02-17 06:10 | 2014-02-18 23:59 | 42
G015199 | RR | C1 | Unit PLC failure | 2014-02-22 06:32 | 2014-02-22 23:59 | 17
G015224 | RR | C9 | River conditions due to Wanapum forebay drafting | 2014-03-02 01:16 | 2014-03-03 23:59 | 47
G015225 | RR | C11 | Due to high head across dam, while drawing down level at Rock Island | 2014-03-02 01:16 | 2014-03-03 23:59 | 47
G015226 | RR | C8 | C-8 declared unavailable due to Wanapum forebay drafting | 2014-03-02 01:16 | 2014-03-03 23:59 | 47
G015227 | RR | C8 | Unavailable due to increased head across the dam, while lowering Rock Island Headwater to assist repairs at Wanapum Dam | 2014-03-02 23:54 | 2014-03-03 23:59 | 24
G015228 | RR | C9 | Unavailable due to increased head across the dam, while lowering Rock Island Headwater to assist repairs at Wanapum Dam | 2014-03-02 23:55 | 2014-03-03 23:59 | 24
G015229 | RR | C11 | Unavailable due to increased head across the dam, while lowering Rock Island Headwater to assist repairs at Wanapum Dam | 2014-03-02 23:55 | 2014-03-03 23:59 | 24
G015238 | RR | C8 | Gross head up to 95.5 feet. | 2014-03-03 22:57 | 2014-03-04 23:59 | 25
G015239 | RR | C9 | Gross head up to 95.5 feet. | 2014-03-03 22:57 | 2014-03-04 23:59 | 25
G015240 | RR | C11 | Gross head up to 95.5 feet. | 2014-03-03 22:57 | 2014-03-04 23:59 | 25
G015244 | RR | C7 | Exciter tripped, unable to reset | 2014-03-07 11:05 | 2014-03-07 23:59 | 13
G015357 | RR | C11 | Unit would not start | 2014-04-20 19:42 | 2014-04-21 23:59 | 28
G015362 | RR | C11 | Burnt smell coming from unit - investigating. | 2014-04-22 04:04 | 2014-06-27 19:00 | 1599
G015427 | RR | C1 | Fish screen needs to be removed from intake. | 2014-05-13 07:00 | 2014-05-13 23:59 | 17
G015433 | RR | C7 | Leak at C-7 Main Transformer. | 2014-05-15 07:00 | 2014-05-16 23:59 | 41
G015483 | RR | C1 | Blade devation lockout | 2014-05-29 19:42 | 2014-05-31 19:00 | 47
G015501 | RR | C4 | Unit out due to PLC failure | 2014-06-05 20:50 | 2014-06-06 23:59 | 27
G015522 | RR | C1 | Tripped to lockout on exciter internal trip | 2014-06-16 19:45 | 2014-06-17 23:59 | 28
G015528 | RR | RR Plant | RC requests RR max cap to 850 MW due to N-1 if Sickler bank opens. Changed to 950MW at 0757, then to 1000MW at 0828. To 950MWs at 0939. | 2014-06-18 05:50 | 2014-06-19 18:00 | 36 | various, see reason column
G015670 | RR | RR Plant | Forced reduction due to loss of transmission resources. | 2014-08-05 16:47 | 2014-08-05 22:45 | 6 | 650
G015671 | RR | RR Plant | Forced reduction due to loss of transmission resources. | 2014-08-05 22:45 | 2014-08-06 03:42 | 5 | 900
G015678 | RR | C06 | Tripped on turbine guide bearing low oil. | 2014-08-09 16:31 | 2014-08-09 22:32 | 6
G015686 | RR | C10 | Failed to start | 2014-08-12 20:41 | 2014-08-13 10:28 | 14
G015819 | RR | C04 | C-4 Turbine Guide Bearing (TGB) oil pot is leaking. Repairs could be performed within the first day, unsure of what we'll find when we drop the pot so we gave ourselves an extra day just in case. | 2014-10-09 07:10 | 2014-10-10 18:29 | 35
G015831 | RR | C03 | Failed to start | 2014-10-15 21:00 | 2014-10-16 15:23 | 18
G015868 | RR | C09 | Turbine Guide Bearing (TGB) leaking oil. | 2014-11-12 06:10 | 2014-11-18 15:34 | 153
G015993 | RR | C03 | Exciter trouble | 2014-11-21 06:50 | 2014-11-22 23:59 | 41
15-00257 | RR | C08 | Large unit repairs concerning the stator, rotor and servo rod assembly. This outage replaced G016088 per Peak RC's request | 01/21/2015 16:38 | 12/13/2017 09:19 | 25360.6833
G016427 | RR | RR Plant | Technicians need to go through units C1 - C7 to remove pre-start on packing flow and to complete governor upgrades. They will only need one unit out at a time and they estimate the duration to be less than one hour per unit. I will subimit another TOA for February 19th however it might be shortened or cancelled depending on how well theTech's do on the 18th. This TOA is reflecting a 105 MW derate from RR's 1255 MW total. | 2015-02-18 08:10 | 2015-02-18 13:37 | 5 | 1150
G016500 | RR | C02 | Dive on surface collector | 2015-03-26 10:10 | 2015-03-26 15:50 | 6
G016568 | RR | C04 | 86 lockout on startup | 2015-04-27 13:41 | 2015-04-28 13:43 | 24
G016569 | RR | C04 | Investigate failures during recent startups. Governor problems: Gate Distributor is not working correctly and needs to be cleaned. | 2015-04-30 07:10 | 2015-05-01 18:37 | 35
G016711 | RR | C10 | Hot smell from windings | 2015-06-24 19:17 |  | 0
G016711 | RR | C10 | COIL FAILURE and STATOR REWIND | 2015-06-24 19:17 | 2016-11-17 07:28 | 12276
G016716 | RR | RR Plant | C-2 trashrack into alarm. Divers needing C-1, C-2 and C-3 outages to safely perform the cleaning. | 2015-07-01 03:09 | 2015-07-01 11:50 | 9 | 950
G016723 | RR | C09 | Breaker pump excessive run time. No prestarts. | 2015-07-06 01:55 | 2015-07-06 06:28 | 5
G016868 | RR | C06 | High Field Voltage. Extending outage for continuation of Rotor damage assessment. Extending outage for repairs and testing. | 2015-08-06 15:24 | 2015-08-28 16:18 | 529
G016996 | RR | C03 | Phase 3 software timeout. | 2015-09-07 02:28 | 2015-09-08 23:59 | 46
G017084 | RR | C06 | Investigate / repair Turbo Vent Valve vibration. | 2015-09-22 08:10 | 2015-09-22 15:18 | 7
G017210 | RR | C06 | Unit breaker problems. | 2015-10-21 15:03 | 2015-10-22 13:08 | 22
G017270 | RR | C03 | To change out C-3 transformer sudden pressure device. | 2015-11-06 07:10 | 2015-11-06 16:20 | 9
G017361 | RR | C02 | Forced Outage resulting from G017236 - Blade Trunnion Gap measurement and Rotor bus bar inspection and Shaft Oil Seal inspection | 2015-12-04 16:51 | 2015-12-11 16:05 | 167
G017401 | RR | C04 | Possible exciter problems, operator investigating. | 2015-12-24 06:14 | 2015-12-24 14:29 | 8
G017402 | RR | C04 | Exciter problems | 2015-12-24 15:06 | 2015-12-26 09:29 | 42
G017603 | RR | C01 | High Trashrack Differential | 2016-03-02 06:30 | 2016-03-07 07:10 | 121 | 85
G017685 | RR | C07 | C-7 tripped the 86 lockout due to turbine guide bearing Hi Hi vibration on start up. | 2016-04-01 06:09 | 2016-04-01 12:48 | 7
G017996 | RR | C09 | COIL FAILURE and STATOR REWIND | 07/14/2016 23:18 | 04/28/2017 13:59 | 6902.6833
G018163 | RR | RR Plant | C06, C04 & C03 THRUST POT INSPECTIONS | 2016-09-13 07:12 | 2016-09-13 14:40 | 7 | 1149
G018164 | RR | RR Plant | C02 & C01 THRUST POT INSPECTIONS | 2016-09-15 07:11 | 2016-09-15 18:50 | 12 | 1149
G018176 | RR | C02 | Field voltage still unstable at startup. | 2016-09-15 20:01 | 2016-09-16 10:47 | 15
G018279 | RR | C05 | 2016 THRUST POT REPAIRS | 2016-10-12 10:01 | 2016-12-02 14:02 | 1228
G018385 | RR | C10 | Unit tripped on high temp | 2016-11-15 18:35 | 2016-11-16 23:59 | 29
G018408 | RR | RR Plant | TRASH RACK CLEANING on C11, C10 and C9 | 2016-11-27 22:12 | 2016-11-28 05:50 | 8 | 1124
G018409 | RR | RR Plant | TRASH RACK CLEANING ON C8, C7, C6 and C5 | 11/28/2016 22:16 | 11/29/2016 05:22 | 7.1
G018410 | RR | RR Plant | TRASH RACK CLEANING ON C6, C5, C4 and C3 | 11/29/2016 22:09 | 11/30/2016 05:44 | 7.5833
G018413 | RR | C10 | C-10 INSPECTION for TGB OIL LEAK | 2016-11-22 08:11 | 2016-11-22 16:50 | 9
G018414 | RR | C10 | C10 TGB SEAL INSPECT & REPLACE As of Wed Nov 23rd I believe the plan is to have this outage take the place of the C-11 outage. | 11/28/2016 05:50 | 12/01/2016 17:36 | 83.7667
G018417 | RR | C11 | Smoke alarm and burnt smell 12/9/16 Return date extended until the end of January. KR 1/5/2017 return date extended until Nov 2018. AS | 11/27/2016 06:29 | 01/26/2017 06:10 | 1439.6833
G018688 | RR | C01 | Turbine shaft is leaking and needs tightened | 03/08/2017 19:35 | 03/09/2017 14:28 | 18.8833
G018738 | RR | C01 | Hi trash rack differential | 03/21/2017 03:11 | 03/22/2017 23:59 | 44.8
17-07028 | RR | C07 | Determine why it failed to start | 2017-04-02 17:45 | 2017-04-03 16:08 | 22.3833
17-07327 | RR | C01 | Head gates will be installed on Monday (5-8-17) and wiremen will then perform rotor and bus cleaning to resolve exciter alarms. Paul Resler has recommended that we not run C1 throughout the weekend so it will remain unavailable until wiremen can perform the necessary cleaning. | 05/05/2017 15:50 | 05/09/2017 19:08 | 99.3
17-07499 | RR | C05 | RR C-5 tripped offline due to Blade Deviation. Would not restart | 06/23/2017 01:24 | 06/23/2017 10:50 | 9.4333
17-07503 | RR | C05 | troubleshooting | 2017-06-23 22:49 | 06/24/2017 09:31 | 10.7
17-07553 | RR | C04 | Failed to start would not build up voltage | 07/14/2017 07:58 | 2017-07-14 13:47 | 5.8167
17-07632 | RR | C02 | Troubleshoot Thrust Bearing Pad Low Pressure | 2017-08-11 01:06 | 2017-08-11 14:51 | 13.75
17-07668 | RR | C04 | Rotor Weld Crack Warranty Extension of iTOA 17-07633 | 2017-08-21 07:15 | 2017-08-25 15:45 | 104.5
17-07830 | RR | C09 | Try to determine what is causing noise on startup | 10/18/2017 09:51 | 11/27/2017 06:10 | 956.3167
17-07888 | RR | C01 | Exciter voltage alarms and rotor cleaning | 11/06/2017 10:59 | 2017-11-09 14:56 | 75.95
17-07930 | RR | C07 | Tech's testing issue of blade/gate deviation and frequency issues. | 12/01/2017 09:07 | 2017-12-01 16:12 | 7.0833
17-07948 | RR | C08 | Large unit repairs concerning the stator, rotor and servo rod assembly. This outage replaced G016088 per Peak RC's request and is a continuation of 15-00257 | 12/13/2017 16:00 | 12/15/2017 14:00 | 46
1-00541113 | RR | C01 | investigate oil leak | 10/01/2018 17:50 | 01/16/2018 09:45 | 6200.0833
1-00602790 | RR | C01 | oil leak | 10/05/2018 23:59 | 10/02/2018 05:07 | 90.8667
| RR | C01 | unit out of service - inspection for seal leaks | 10/02/2018 05:07 | 10/01/2018 17:50 | 11.2833
1-00601762 | RR | C02 | Troubleshoot exciter issues on shutdown | 09/29/2018 23:59 | 09/28/2018 05:06 | 42.8833
1-00543055 | RR | C02 | shaft seal packing adjustment | 01/19/2018 15:50 | 01/19/2018 14:10 | 1.6667
1-00548793 | RR | C02 | Repair ground | 02/18/2018 23:59 | 02/15/2018 07:02 | 88.95
1-00617008 | RR | C02 | C2 unavailable due to water in the turbine guide bearing oil. | 12/13/2018 23:59 | 12/12/2018 02:07 | 45.8667
1-00620704 | RR | C03 | Troubleshoot the brushes rubbing on the slip rings. | 12/31/2018 17:50 | 12/24/2018 12:15 | 173.5833
1-00602829 | RR | C03 | Change out the oil in the turbine guide bearing on C-3 | 10/03/2018 23:59 | 10/02/2018 13:36 | 34.3833
1-00545853 | RR | C04 | Turbine guide bearing problems | 02/01/2018 17:50 | 02/01/2018 14:08 | 3.7
1-00591184 | RR | C05 | C05 failed to start. Reason unknown. | 08/17/2018 23:59 | 08/16/2018 11:42 | 36.2833
1-00595058 | RR | C05 | Troubleshoot Mech lockout on shutdown | 08/31/2018 23:59 | 08/30/2018 03:51 | 44.1333
1-00591156 | RR | C05 | Plant mechanics to clean SVE on C5. | 08/16/2018 11:50 | 08/16/2018 09:10 | 2.6667
1-00598640 | RR | C07 | Troubleshoot unit trip | 09/19/2018 23:59 | 09/18/2018 08:09 | 39.8333
1-00596238 | RR | C07 | Troubleshoot and restore. | 09/06/2018 23:59 | 09/05/2018 17:11 | 30.8
| RR | C07 | Change oil on turbine guide bearing | 09/11/2018 23:59 | 09/10/2018 08:15 | 39.7333
1-00544196 | RR | C08 | Extension of previous outage. Unit is making a knocking sound. Dewatering unit to investigate. | 02/09/2018 23:59 | 01/28/2018 17:50 | 294.15
1-00571354 | RR | C08 | Wiremen, Techs and Engineers are troubleshooting C8. New Sync Transducer was installed but the unit is not able to start back up. Problem is unknown at this time. | 05/24/2018 13:50 | 05/23/2018 09:50 | 28
1-00572294 | RR | C08 | Unit will need to be dewatered to complete repairs on packing. | 06/18/2018 16:50 | 05/25/2018 13:50 | 579
| RR | C08 | Exciter repair | 09/13/2018 23:59 | 09/12/2018 06:50 | 41.15
1-00569807 | RR | C10 | Investigate vibration shutdown | 05/16/2018 23:59 | 05/14/2018 14:11 | 57.8
| RR | C10 | Tripped offline. Reason unknown. | 06/09/2018 09:50 | 06/09/2018 09:33 | 0.28333
1-00559039 | RR | C10 | Head cover packing | 03/30/2018 23:59 | 03/29/2018 11:05 | 36.9
| RR | C10 | unknown | 05/14/2018 23:59 | 05/13/2018 23:58 | 24.0167
1-00620372 | RR | C10 | Broken Shear Pin | 12/26/2018 23:59 | 12/25/2018 09:40 | 38.3167
1-00570507 | RR | C11 | Troubleshoot unit trip and the smell of smoke | 05/18/2018 23:59 | 05/17/2018 19:19 | 28.6667
1-00593201 | RR | C11 | Gas up breaker. | 08/22/2018 11:50 | 08/22/2018 08:30 | 3.3333
1-00593875 | RR | C11 | Repair SF6 leak | 08/25/2018 17:00 | 08/24/2018 08:06 | 32.9
1-00599581 | RR | RR Plant | Trash Rack Clam stuck in front of C-3 | 09/22/2018 23:59 | 09/21/2018 13:45 | 34.2333
| RR | C01 | 7099 - Other turbine problems | 2019-01-01 | 2019-12-31 23:59 | 8759.9833
| RR | C09 | 4830 - Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 2019-01-01 | 2019-12-31 23:59 | 8759.9833
| RR | C03 | 9300 - Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 2019-07-22 19:26 | 2019-07-27 08:02 | 108.6
| RR | C04 | 3620 - Main transformer | 2019-07-22 19:26 | 2019-07-26 16:20 | 92.9
| RR | C06 | 4551 - Generator bearings | 2019-08-28 16:54 | 2019-09-19 10:15 | 521.35
| RR | C08 | 7050 - Turbine governor | 2019-09-06 21:21 | 2019-09-11 18:47 | 117.4333
| RR | C10 | 3618 - Other switchyard equipment ? (not outside management control) | 2019-09-11 07:10 | 2019-09-11 18:05 | 10.9167
| RR | C11 | 3618 - Other switchyard equipment ? (not outside management control) | 2019-09-11 07:10 | 2019-09-11 18:05 | 10.9167
| RR | C08 | 7007 - Bearings A | 2019-09-18 07:50 | 2019-10-01 15:33 | 319.7167
| RR | C07 | 4551 - Generator bearings | 2019-09-27 16:18 | 2019-12-31 23:59 | 2287.6833
| RR | C02 | 7099 - Other turbine problems | 2019-10-11 15:47 | 2019-12-31 23:59 | 1952.2
| RR | C11 | 7099 - Other turbine problems | 2019-10-11 16:19 | 2019-10-18 08:43 | 160.4
| RR | C06 | 4550 - Generator bearings and lube oil system (including thrust bearings on hydro units) | 2019-12-18 19:43 | 2019-12-20 15:28 | 43.75
| RR | C01 | 7099 - Other turbine problems | 2020-01-01 | 2020-03-13 16:25 | 1744.4167
| RR | C02 | 7099 - Other turbine problems | 2020-01-01 | 2020-01-24 06:50 | 558.8333
| RR | C03 | 7099 - Other turbine problems | 2020-01-01 | 2020-02-27 07:34 | 1375.5667
| RR | C07 | 4560 - Generator vibration (excluding vibration due to failed bearing and other components) | 2020-01-01 | 2020-03-05 | 1536
| RR | C02 | 9015 - Pandemic | 2020-03-23 15:30 | 2020-04-30 06:00 | 902.5
| RR | C07 | 9015 - Pandemic | 2020-03-23 15:30 | 2020-04-30 06:00 | 902.5
| RR | C04 | 4550 - Generator bearings and lube oil system (including thrust bearings on hydro units) | 2020-03-28 07:18 | 2020-03-30 12:58 | 53.6667
| RR | C11 | 7099 - Other turbine problems | 2020-03-28 15:02 | 2020-03-28 23:47 | 8.75
| RR | C05 | 7099 - Other turbine problems | 2020-04-10 17:46 | 2020-04-11 10:11 | 16.4167
| RR | C11 | 7099 - Other turbine problems | 2020-04-24 09:03 | 2020-04-24 15:13 | 6.1667
| RR | C11 | 7099 - Other turbine problems | 2020-04-28 10:04 | 2020-04-28 16:39 | 6.5833
| RR | C09 | 7050 - Turbine governor | 2020-06-30 15:48 | 2020-07-01 14:27 | 22.65
| RR | C11 | 7099 - Other turbine problems | 2020-07-22 17:50 | 2020-08-06 11:02 | 353.2
| RR | C09 | 3982 - PLC - hardware problems (including card failure) | 2020-09-22 23:13 | 2020-09-23 10:01 | 10.8
| RR | C10 | 4551 - Generator bearings | 2020-09-25 09:01 | 2020-09-25 14:32 | 5.5167
| RR | C05 | 4810 - Generator output breaker | 2020-11-09 21:26 | 2020-11-12 15:28 | 66.0333